Micro Gas Turbine

Technology

Research and

Development

for European

Collaboration

Technology Summary

# Acknowledgments

The Micro Gas Turbine Technology Summary has been produced by a technical Working Group composed by MGT OEMs, Heat Exchangers Manufacturers and R&D Institutes coordinated by the European Turbine Network (ETN). This document aims to identify a number of key areas that require substantial R&D efforts for micro gas turbines from the European community to become competitive in the energy sector worldwide.

Contributions to this document were provided by the organisations listed below:

| Aurelia Turbines |  | ACTE |  | Ansaldo Energia |  |
| --- | --- | --- | --- | --- | --- |
| Bladon Jets |  | Berlin Partner |  | Bosal |  |
| Capstone |  | DLR |  | Delta Motorsport |  |
| Compower |  | ENEA |  | Euro-K |  |
| DGTA |  | Hieta |  | HiFlux |  |
| Fraunhofer |  | INNECS |  | IMP PAN |  |
| IRIS |  | Mitis |  | MTT |  |
| KTH |  | Price Induction |  | Samad Power |  |
| RSE |  | Cranfield University |  | City University London |  |
| Brandenburg University of Technology |  | Karlsruhe Institute of Technology |  | Technical University of Berlin |  |
| École Centrale Lyon |  | Universidad de Sevilla |  | Universita Roma TRE |  |
| Technical University of Delft |  | University of Genoa |  | University of Leeds |  |
| Vrije Universiteit Brussel |  |  |  |  |  |

# Introduction

The Micro Gas Turbine (MGT) Technology Summary has been produced by a technical Working Group composed by MGT OEMs, Heat Exchanger Manufacturers and R&D Institutes coordinated by the European Turbine Network (ETN). The Working Group aims to bring together MGT experts to assess the development and market deployment of MGT technology.

The goal of this detailed summary is to encourage investment by EU Industries and decision makers into further research and development for MGT-related technologies.

The first part of the paper provides an overview of the MGT and the challenges in developing the technology further in terms of system optimization, material selection, reduction of production costs, reduction of maintenance and part replacement costs, life extension and hence reducing the environmental impact from system and part manufacturing. The document also analyses the results of international research projects.

The second part of the paper explains how a MGT can contribute to reaching the EU 2030 Climate and Energy targets when installed in Combined Heat & Power (CHP) and Renewable Energy Source (RES) projects.

The Expected Impact chapter analyses the potential of MGT projects to increase energy savings, reduce CO emissions, and ease the integration of the RES into the power grid through their highly flexible nature.

This paper then concludes by providing a set of short term and long term research activities that would significantly assist in the development and deployment of MGT technologies.

Contents

Acknowledgments	3

1	Introduction	4

2	Vision	7

2.1	MGT in the EU Energy Scenario	8

2.2	Integration with Renewable Energy Sources	9

2.2.1	Bioenergy	9

2.2.2	Concentrated Solar Power	10

2.2.3	Fuel Cells	11

3	MGT Technology	13

3.1	Definition	13

3.2	Applications	16

3.2.1	Energy	16

3.2.2	Transportation	18

3.3	Technology Background	19

3.4	Technology Description	20

3.5	Comparison with Other Technologies	24

3.6	Technology Challenges	26

3.6.1	Turbomachinery	26

3.6.2	Combustion	28

3.6.3	Materials	35

3.6.4	Recuperator	39

3.6.5	System Integration	43

3.7	International Developments	49

4	Expected Impacts	52

4.1	Energy Saving	52

4.2	Emission Reduction	54

4.3	Financial Cost/Benefit Analysis	54

4.4	Partnering with RES	56

5	Policy Context	59

5.1	EU Policy Framework	59

5.2	Policy Recommendations	60

6	Requirements on Deployment	61

6.1	Investment and Market Barriers	61

6.2	Recommendations & Important area of cooperation	63

6.2.1	Recuperator	63

6.2.2	Turbomachinery	64

6.2.3	Combustion system	65

6.2.4	Power electronics	66

7	Bibliography	67

# Vision

The UNFCCC COP-21 has set the worldwide pace for the development of the next generation of energy systems. Simultaneously, the EU countries have accepted the EU 2030 Climate and Energy package, establishing the following targets:

- At least 40% greenhouse gas (GHG) emissions reduction from 1990 levels by 2030;

- At least 32.5% energy efficiency increase by 2030;

- At least 32% renewable energy share by 2030;

- 15% increased energy interconnections between member states by 2030.

In this context, small scale power and heat generating technologies could play a crucial role in reducing short and long term GHG emissions (by 80-95% by 2050 compared to 1990 levels). Among the competing emerging technologies, Micro Gas Turbines (MGT) have the capability to help meet the above mentioned energy targets with cost competitive, low emission, fuel efficient and fuel flexible characteristics. With these characteristics, MGTs can also support the increasing share of renewables to meet the challenges of the modern electricity grid.

Compact size, light weight, low maintenance, low noise, low emissions and multi-fuel capabilities make the MGT not only a transition technology for the EU’s ambitious 2030 Energy targets, but also a prime mover of the future for competitive, secure and sustainable micro-scale polygeneration.

The opportunities for MGTs extend into many industries and environments, including micro-CHP (Combined Heat & Power), portable power generation, marine auxiliary power, standby power, range extenders in hybrid vehicles, auxiliary power units in heavy vehicles, and small, unmanned air vehicles (UAVs). Given their high flexibility, the latest research and development activities have focused on hybrid MGT applications; for example, coupling MGTs with a Concentrated Solar Power (CSP) dish or with a Solid Oxide Fuel Cell (SOFC). Successful hybrid systems may further decarbonize the EU energy system while assuring the security of the energy supply and back-up capabilities.

Though the MGT market is still considered a niche market, the recent development of MGT systems for households could set up a new energy scenario in which industrial, commercial and residential customers produce power, heating and cooling in line with the decarbonisation of the energy system. However, to boost this technology to its full potential, the support of EU institutions, significant investments, R&D activities, and policy updates are required to promote a stable business climate that encourages low-carbon investments.

Europe can lead this technology development and transition with cooperation between industry and research institutes/universities supported by the EU.

## MGT in the EU Energy Scenario

Due to the high share of renewables, the EU energy system is moving towards decentralised power and heat generation. The role of the Utilities and independent power producers is changing as more rooftops deploy solar, more wind and hydro energy go online, and more micro-scale combined heat and power plants are put in place.

Among the challenges derived from a higher share of renewables is the intermittent generation of wind and solar energy sources. This challenge currently serves as a main driver for the implementation of MGT systems due to their ability to provide fast and reliable power, helping to guarantee for grid stability.

Figure 2-1: MGT in the Energy System

A decentralised power generation scenario integrating micro gas turbines along with wind turbines, photovoltaic systems, biomass plants, fuel cells and energy storage would provide a secure, stable, efficient, economical and environmentally friendly on-site energy production system, connected close to the consumers load and providing the end consumer with heat and electricity without major transportation and conversion losses. An important advantage of micro gas turbines to other heat engines for decentralised power generation is their capability to burn a variety of fuels, ranging from natural gas, diesel, LPG and hydrogen, to waste and biomass-derived fuels like landfill gas or gasification products from biomass. As a micro-scale fuel flexible system, MGT could play an essential role in the future energy scenario to guarantee security of supply and sustainable cost-efficient energy generation.

Given their Combined Heat and Power (CHP) configurations, and ability to integrate with RES, MGT technologies have been acknowledged by the European Parliament in its resolution on an EU Strategy on Heating and Cooling (2016/2058(INI)). Adapting the current energy scenario into a truly sustainable one will require realizing the full potential for renewable energy sources to satisfy the energy scenario’s heating and cooling demand. This will require equal effort from both the generation and end-use sectors in order to achieve the ambitious targets set for 2030.

In the short term, the MGT technology can absorb the fluctuations of the Renewable Energy Sources (RES) by using natural gas, hydrogen, biogas, industry waste gas, landfill gas, etc. In the long term, the fuel flexibility of MGT applications can assure high utilisation of RES while helping to ensure security of the energy supply by operating with natural gas or other fuel sources when RES are not available.

In the first decade of the twenty-first century, MGT proved to be reliable and able to perform satisfactorily; delivering over 30% electrical efficiency at full load, with an overall efficiency around 80% in a CHP configuration, NOx values below 15 ppm at 15% O2, and an availability over 90% for a unit cost level of 800 €/kW [1]. For catalytic combustors, levels of 3 ppm NOx have also been reported, though further developments are needed to extend the lifetime of the component.

The performance targets of MGTs should be improved to better fit into the EU energy scenario. Areas of performance improvement include fuel-to-electricity efficiencies of 40% or higher, capital costs less than 500 €/kW, NOx emissions reduced to single digit parts-per-million levels, and an increase in the operation between overhauls to between 1 and 2 years.

## Integration with Renewable Energy Sources

In the future, the energy supply will rely significantly on renewable energy sources. With increased deployment of intermittent, non-dispatchable renewable energy projects, larger fluctuations in electricity supply will be introduced. Furthermore, the fluctuating and uncertain outputs of RES are bound to specific locations. This calls for back-up systems and hybrid technologies to secure and flatten the outputs. If the EU is to lead the transition and meet its ambitious energy targets, a special focus on MGT technology is needed to develop its full fuel flexible potential and its ability to accommodate other technologies in an integrated system.

### Bioenergy

Figure 2-2: Ansaldo Turbec T100 running with biogas

The use of biomass instead of fossil fuels has been considered for MGTs since their entrance in the power generation market. The ability of MGTs to operate with a wider range of fuels already makes this technology an attractive solution for biogas applications, agricultural and food waste, food processing, breweries, landfills, waste water treatment plants and human waste treatment. [2] Proven deployment of MGTs in the biogas field is already a reality, with companies such as NewEnCo operating over 30 Turbec T100 units on untreated biogas fuel for more than 55,000 hours with an overall efficiency of 80% and exceeding 94% availability [3].

Since bioenergy resources are location-specific and often scarce, fuel availability has become a market driver for MGT technology. This has resulted in a need for versatile energy conversion technologies in the micro scale (below 500 kW) in order to economically develop the full potential of bioenergy sources. The fuel flexibility of the MGT can help overcome most of the current technical challenges and make the biomass systems more economically attractive. In fact, increased fuel flexibility can help ensure that cheaper fuels may be used when available, and that fuel storage and conditioning can be minimized. The fuel mix can be also changed based on varying market conditions. A large variety of suitable fuels also makes the technology usable in a wider geographic area. The decentralized application of MGT technologies also supports the development of local biomass feedstock use, bringing additional economic activities to the supply chain in rural areas.

In 2013, biomass contributed 15% of the total EU primary energy production, with only 3% of the solid biomass being imported from outside the EU, indicating that biomass is mainly a local fuel. Biomass supplied 14,7% of EU heat and 7,5% of electricity in the EU [4]. Many countries, especially in the eastern and northern EU, are depending on biomass to help meet the 2020 goals in their National Renewable Energy Action Plans. As such, CHP applications using a wide range of biofuels are one of the priorities of H2020 Programme.  These CHP applications have also been recognized by the European Strategic Energy Technology Plan (SET-Plan) for their potential contribution to meeting the CO2 reduction goals of 2020, 2030 and beyond, resulting in a targeted increase in renewable energy-based co-generation.

Though biomass power generation technologies are more expensive, with some technological barriers to overcome, the ability of MGTs to utilise varying compositions of liquid and gaseous fuels [5], as opposed to other competitive technologies, provides an opportunity to reduce GHG emissions while lowering the cost of energy. At the same time, using indigenous feedstocks increases the self-sufficiency of the EU energy system. Biomass CHP could also be used to balance the intermittency of other renewables, and the varying heat/power ratio can be used to combat seasonal differences in heat and electricity demand.

### Concentrated Solar Power

Concentrated Solar Power (CSP) is a technology that converges a large area of sunlight into a smaller area. That heat source can subsequently be used to generate electricity. CSP from solar dish configurations can elevate the temperature of a working fluid to the range of 800-1000°C. Working fluids within this temperature range may allow a MGT to efficiency integrate with a CSP system to create a reliable, long-life, low noise and low maintenance power generation system.

Such a system could operate both in a stand-alone configuration, providing eco-friendly electricity in remote locations or connected to the grid, or in a multi-system “farm” arrangement to provide higher outputs.

Figure 2-3: CSP dishes in farm arrangement

Currently, the Stirling engine is the most common technology used for micro-scale solar dish CSP applications. However, this engine suffers from a number of technical problems affecting life and reliability, such as cylinder seal issues, hot spots in the heater, and difficulties with part-load control. Solutions to these issues will lead to additional system complexity and increased costs. Nevertheless, an integrated MGT/CSP system could be a potential alternative technology in this field when compared to a traditional Internal Combustion Engine (ICE), since the basic engine cycle and design principles of an ICE are not compatible with the working fluid of a CSP system.

Figure 2-4: OMSoP system

Figure 2-5: BiostirlingSka system

The main components for a MGT-based CSP system are the dish concentrator, the receiver unit and the MGT. All three components are independently available today either commercially or in conceptual form, but they have not been developed to operate together in the target power range. An integrated system, designed to produce 3-10 kWe, has been demonstrated at large scale with the OMSoP project, funded by EU under the H2020 Working Programme.

In recent years, there is increased interest in developing technologies that can handle renewable energy sources while providing dispatchable power. One of the objectives of the OMSoP project is to demonstrate that a MGT technology can be hybridized to utilize both solar heat input and natural gas to provide dispatchable, continuous, reliable and stable power with a high share of solar power, when available. This characteristic makes MGT distinguishably competitive against photovoltaic technologies. Future research activities could focus on the integration of the system with thermal storage technologies and/or an absorption chiller for polygeneration.

### Fuel Cells

The concept of hybridising a MGT with a fuel cell has been in development since MGTs were first applied in the power generation sector, though the commercialisation of such a system was never completed due to the high costs of the technology and the novelty of the fuel cells.

There are different types of fuel cells that can be hybridised with MGTs, however the hybridisation with SOFC seems to be the most suitable, as this works at temperatures of about 950˚C, which is high enough to operate a micro gas turbine. Furthermore the exhaust gases of the turbine can be utilised to preheat the fuel cell. Considering that the fuel utilisation of a SOFC is about 80% to 85% [6], it is possible to burn the exhaust gas of the fuel cells in the combustion chamber of the turbine.

The world’s first hybrid MGT/SOFC system, with a power output of 220 kW (200 kW from the SOFC and 20 kW from the MGT) was installed in 2005 at the University of California, Davis. The system demonstrated an electrical efficiency of 53%.

Figure 2-6: Hybrid System SOFC/MGT (220kW)

In the past, the size of the fuel cell, the high cost of the system, and the low demand on the market for decentralised power generation has hindered the development of this technology. Now, however, the shift towards a decentralised power generation market, the increase of fuel cell output and the decrease of its volume, coupled with increased MGT efficiency and fuel flexibility, makes this system a promising technology for distributed power supply.

The integration of MGT and SOFC technologies may be direct or indirect. In an indirect configuration, the coupling of the two components is done via a heat exchanger, presenting temperature limitation issues. With direct integration, the exhaust of the fuel cell is used to heat the air from the MGT compressor. Additional fuel may then be used by the MGT to optimize its operation for a gain in efficiency. Such an optimized configuration has the potential to yield an efficiency of about 73%.

Figure 2-7: Hybrid system emulator of the BioHypp

Research activities for the integration of these two technologies are still ongoing. For example, the European Commission has funded the BioHypp (Biogas-fired Combined Hybrid Heat and Power Plant) project within the Horizon 2020 Work Programme. The main objective of this project is to develop and realise a full-scale technology demonstrator of a hybrid power plant in a lab environment suitable for gaseous sustainable biomass feedstock derived from fermentation processes. Realising this system will validate the great potential of the hybrid plant concept as an efficient and energy-sustainable source of heat and electrical power.

# MGT Technology

## Definition

Micro Gas Turbines (MGT) are complex systems, developed on either the Ericsson cycle or the Brayton cycle, used for micro-scale power generation at one point in a distributed network or at a remote location. These devices can be used in stationary, transport or auxiliary power applications.

The European Turbine Network (ETN) refers to a system-based definition for micro gas turbines, whereby MGT are small gas turbines combined with a high speed generator. The authors recognise that this definition does not define the output range; however, the technological requirement of a high speed generator for gas turbines is inherent of the micro/small scale. In this regard, these systems do not typically exceed 500 kWe.

In the literature, the prefix “micro” can refer to different output ranges depending on the source, and therefore, the actual boundary between a micro, small and large gas turbine is vague. Some authors refer to micro scale systems as units with power outputs between 3 to 250 kW or 300 kW while other reports label MGT as any gas turbine below 1 MW. The European Union, on the other hand, defines a micro-cogeneration unit based on the electrical power output with a maximum capacity below 50kWe. Their boundary for small-scale units is set to a maximum of 1MWe. In addition to differences based on the range of output, the types of output (shaft, electrical or thermal output) may also vary, or not be mentioned in many cases.

A MGT typically includes the following components: compressor, turbine, combustor, bearings, recuperator, high speed generator, power conditioning and control unit, enclosure and balance-of-plant [7]. Some of these components might not exist in a particular MGT, and may depend on the type of application and requirements of the system.

Micro gas turbine main characteristics are:

- Electrical Output: 3 to 500 kWe

- Thermal Output:  3 to 1,500 kWth and exhaust gas temperature between 250-300 ºC

- Fuel flexibility: Natural gas, hydrogen, sour gas, gasoline, kerosene, diesel fuels, heating oil

- Electrical efficiency range: 23-40%

- Total efficiency (CHP) range: 80-90%

- Reliability and life: 40,000 to 80,000 hours before overhaul

- Emissions: Below 9 ppmv for NOx on fossil fuels. Noise levels below 50 dBA

- Modularity: Ability to group units in farm arrangement to share equipment and infrastructures.

- Low weight: 23-30 kg/kW

- Compact system: 0.045-0.065 m3/kWe

- Low maintenance: Typically single radial stage and single rotating part

- Air cooled

Figure 3-1: Ansaldo Energia T100 MGT system for CHP applications

Figure 3-2: Sectional drawing Ansaldo Energia T100

Figure 3-3: Capstone C65 sectional drawing

With regards to the MGT costs, it must be noted that the power range and volumes affect the cost distribution. For a power range between 1 – 10 kW, the table below shows the production cost for the individual components

The cost of the various components or subsystems ranges from:

- compressor and turbine  				13-15 %

- combustor                                  		 	8-11%

- bearings                                       		 	3-4 %

- recuperator                       				21-24 %

- high speed generator 					9-11 %

- power conditioning and control unit 			22-24 %

- enclosure and balance-of-plant	               	17-20%

For power range between 100-300kW, the split of the cost is the following:

- compressor and turbine  				25%

- combustor                                  		 	8%

- bearings                                       		 	1%

- recuperator                       				25%

- high speed generator 					5%

- power conditioning and control unit 			25%

- enclosure and balance-of-plant	               	11%

## Applications

Relative to other technologies for small-scale power generation, micro gas turbines offer a number of advantages, including: a small number of moving parts, compact size, light weight, low emissions, low electricity costs, reliable operation, potential for low-cost mass production, and opportunities to utilise waste fuels and energy recovery. They have been commonly used in many engineering fields and have already been proven to be reliable and working satisfactory [1], suitable for integration with other systems or as a subsystem in a larger energy system.

Micro gas turbine sellers tend to focus on commercial sectors where there is a need for cost-effective electrical and thermal power, such as hotels, schools, hospitals, retail shops and office buildings. MGTs are also an attractive option for remote and reliable electrical power generation for telecommunication, mining, humanitarian missions or military applications.

MGTs also operate in resource recovery operations at oil and gas production fields, wellheads, coal mines, and landfill operations using the by-product gases as fuel. MGTs can also provide thermal oxidation of very low Btu fuels, such as landfill or waste gases, generating a useful electrical output.

Although variable due to market trends and the economic climate, oil and gas applications represent typically 50% of the MGT market for the largest manufacturer Capstone, 40% represents commercial and industrial CHP, 8-9% is applied in renewable energy applications and the last 1-2% covers other markets such as hybrid vehicles or marine applications [2].

### Energy

Power generation

For ground-based power generation, there is competition from many alternative technologies such as small piston engines, fuels cells and Stirling engines. All these technologies focus on energy savings, often utilise cogeneration configurations. Since small scale MGT electrical efficiency is often lower than many alternative prime movers, especially when below 100kW, MGT competitiveness is maintained by utilizing the specific benefits of the gas turbine, including fuel flexibility, power density, low emissions, and low noise.

Remote Power

Figure 3-4: SCADA Metering station for Oil & Gas operations

MGTs can provide electrical power for remote applications where access to the power grid would be too costly or inexistent. Examples include rural, desert or marine environments. They can then operate as a stand-alone unit in an off-grid application or grouped in a farm arrangement to generate higher output and provide electrical power support to a local microgrid. MGTs also offer flexibility in operation, fuels, connection methods, modularity, stable and reliable operation, and lower emissions than alternative generation systems, making them suitable for both off-shore and on-shore oil and gas applications.

Energy Savings

MGTs can also be connected to the grid to perform peak shaving. This is especially attractive for commercial applications. When the power usage peaks, the MGT operator can reduce electricity costs by generating the additional load in a short time. The inherent characteristics of this technology (compact size, low emissions, and low noise emissions) allow the system to operate where other power generation units would not be capable.

Critical Power

Additionally, micro gas turbines are used as back-up power or as part of uninterruptible power supply systems. They can provide a continuous, high quality electrical supply in power-sensitive commercial applications such as data centres, hospitals or telecommunications. The application of micro gas turbines as back-up power generation is attractive for any business where power shut-downs result in significant loss of revenue or damage to assets.

Polygeneration

Micro gas turbines used in co-generative applications have proven to be a promising technical solution for high efficiency energy conversion. These comprise both Combined Heat and Power (CHP) and Combined Cooling/Heating and Power (CCHP). The exhaust gas temperature of micro gas turbines, commonly around 300ºC, can be used directly for heating and industrial processes or be recovered in a heat recovery boiler (CHP) or an absorption chiller (CCHP). Cogeneration MGTs have been installed in commercial environments such as hotels, schools, hospitals or retail shops, as well as industrial locations such as food and manufacturing facilities, for small operations needing hot water or low pressure steam. The use of the exhaust gas temperature allows MGTs to significantly increase their overall efficiency up to 90%, making them an attractive solution for applications that require their range of electrical to thermal output ratio.

For example, Turbec T100 CHP units were installed in 2016 at the Leafy Resort Wellness Spa in Gargnano, Italy. The units provide an electrical availability of 200 kWe and a thermal availability of 300 kWth, and are installed with an absorption chiller, a biomass boiler and a high-efficiency natural gas boiler.

Figure 3-5: Turbec T100 units at Leafy Resort Wellness Spa for CCHP

### Transportation

Range Extender

Electric vehicles biggest challenges are their limitation in battery capacity, where Li-ion batteries are two orders of magnitude lower in specific energy (MJ/kg) than conventional gasoline fuel. This significantly reduces the electric vehicles range and implies a larger number of stops for recharging the batteries. A solution to this problem is the use of micro gas turbines to recharge the batteries when these are close to being empty. The micro gas turbine can operate at optimum load, providing an efficient and low emission on-board recharging system for the electric vehicle. This is especially applicable to transit buses and heavy-duty trucks.

As an example, Capstone has deployed its 30 and 65 kW MGTs in multiple vehicle types, from automobiles to buses to heavy-duty trucks.  Below is an example vehicle integration done by Langford Performance Engineering in the UK.  This vehicle uses a C30 liquid fuelled MGT in a Ford S-Max to create a plugin hybrid. The C30 kicks in after 40 miles, extending the electric range by working to charge to the lithium batteries.

Figure 3-6: Class 7 Series Hybrid with 65kW Micro Gas Turbine Range Extender

Capstone also integrated a C65 into a Class 7 box body truck, in partnership with Kenworth Truck Company, the South Coast Air Quality Management District, and the San Joaquin Valley Air Pollution Control District.  This demonstration truck is able to operate about 20 miles on its lithum-ion batteries, before the micro gas turbine is required to extend range to over 200 miles.

Figure 3-6: Class 7 Series Hybrid with 65kW Micro Gas Turbine Range Extender

Figure 3-6: Tandem drive truck with Route powertrain using Fulcrum turbine (80kW)

UAV/small aircraft propulsion

For aircraft and Unmanned Aerial Vehicle (UAV) propulsion applications, there is a rapidly growing demand for small scale, light and efficient propulsion systems. The largest customer in this market is the military, which means information on development projects is mostly classified. However, also the civil UAV market is growing rapidly and may eventually inherit technology from the military projects. Likewise, the military sector may be the largest contributor of resources for MGT development.  As a result, future ground-based MGT technologies may evolve from aircraft UAV engine designs, similar to current aero-derivative industrial gas turbines, benefitting from improvements in engine endurance and efficiency.

Figure 3-7: UAV Turbines

## Technology Background

The development of the MGT started in the late 1980ies. An important driver was the automotive industry’s effort to development small gas turbines with mechanical drives as an alternative for diesel and gasoline engines (internal combustion engines – ICE). The automotive industry intended to take advantage of the gas turbine’s low emissions, fuel flexibility, and potential to compete on cost with an ICE. Connected to a high speed generator instead of mechanical drive, the technology became very suitable of use in hybrid vehicles. However, at that time (1990ies), the hybrid electrical drive train technology was not yet mature enough for the market.

Instead, other non-automotive companies picked up the MGT technology and introduced it to the decentralized power generation market where its long life and low maintenance cost could compensate for a higher first cost. As a result, decentralised power generation is now a fast growing global market.

1980s

2000s

DOE AGT Project

MGT for automotive industry

Turbogenerator

for electrical industry

1990s

1993-96

EU AGATA Project

Turbochargers

for automotive industry

2016

MGT

for Distributed Power Generation

Figure 3-8: MGT Technology development

## Technology Description

MGTs operate either on the Brayton or on the Ericsson cycle. This is the simplest form of a gas turbine cycle: air at atmospheric conditions is compressed, fuel is added and burned at constant pressure, and then the compressed and heated air is expanded through the turbine back to atmospheric pressure. The recuperated form of this cycle saves fuel by recuperating heat from the exhaust gases and exchanging it with the relatively cool air from the compressor by means of a gas-to-gas heat exchanger.

MGTs differ from larger gas turbines, however, in several operating and system characteristics. First of all, MGTs are significantly smaller in size and output than a large gas turbine, hence their name. Large gas turbines typically measure around 10x3x3 m3 with electrical outputs ranging from 2 to 500 MW, whereas MGT dimensions are around 3x1x2 m3 with power outputs below 1 MW.

MGTs operate at significantly higher revolutions-per-minute. With smaller size, typical problems such as supersonic tip speeds or mechanical limits are delayed to higher rotational speeds. Therefore, a MGT can operate up to 140,000 rpm, whereas a larger gas turbine will typically operate in the range of 3,000 to 20,000 rpm.

Additionally, because of their reduced size, MGTs typically utilise a single radial compressor stage delivering a pressure ratio between 2 and 5. These provide reasonable stage efficiency and a more compact design. Larger gas turbines would operate several axial compressor stages, allowing pressure ratios up to 25.

Combustion temperatures are also reduced for MGTs, ranging between 900 to 1000 ºC. whereas larger gas turbines reach turbine inlet temperatures of 1500 ºC. This is mainly due to the fact that cooling MGTs is expensive and difficult.

MGTs are, as expected, less efficient than larger industrial gas turbines, where the larger dimensions allow many technical inefficiencies to be overcome. Therefore, in order to increase their overall efficiency, MGTs units typically include a recuperator after the turbine.  Additionally, the compact size and simple design of a MGT allows for significant benefits such as easy installation, modularity, use of air bearings, low maintenance, and simple operation.  Furthermore, the lower pressure ratio and combustion temperatures make it easier for a MGT to achieve low NOX emissions.

Several competing manufacturers are developing units in the 25-250 kWe range. Multiple units can be integrated to produce higher electrical output while providing additional reliability should one need repair or maintenance. Most manufacturers are pursuing a design where the compressor, turbine and generator are mounted on a single shaft supported on lubrication-free air bearings and operating at speeds of up to 120,000 rpm.

A schematic diagram of the ANSALDO AEN-T100 is illustrated below:

Figure 3-9: Schematic diagram Ansaldo AEN-T100 with CHP

Typical operating conditions for the AEN-T100 are:

- Combustion chamber pressure = 4.5 bar

- Turbine Inlet Temperature = 950 °C

- Turbine exit gas temperature = 620-650 °C

- Exhaust gases temperature = 80 °C

- Rotation speed = 70000 rpm

- Electrical efficiency = 30±2%

- Total efficiency (CHP) = 80%

Compressor and Turbine

MGT compressors and turbines are typically single stage radial designs that allow for a compact design and higher efficiency in small scale. Axial stages are commonly more efficient than radial stages; however, this is not the case for small scale as the blade height for axial stages would be impractical.

Additionally, the MGT compressor, shaft and turbine are manufactured as a single part which significantly eases maintenance activities. They commonly operate on oil-lubricated or air bearings. Oil-lubricated bearings are a proven and developed technology, however it requires all the associated systems for oil (pump, filter and cooling) and therefore increase design, manufacturing and maintenance costs. Air bearing systems are simpler in design and maintenance, making them a very attractive solution for micro gas turbines.

Figure 3-10: MGT Turbine

Figure 3-11: MGT compressor

Bearing Designs

Commercially available MGTs operate on either oil-lubricated or air bearings. Oil-lubricated bearings are a proven and developed technology, however they require all the associated systems for oil (pump, filter and cooling) and therefore increase design, manufacturing and maintenance costs. Air bearing systems are simpler in design and maintenance, making them a very attractive solution for MGTs.  The Capstone MGTs have utilized specially-designed air bearings since beginning commercial production in 1998, accumulating more than 125 million hours of successful operation.  An example radial air bearing is shown below.

Figure 3-11: Radial Air Bearing Design showing Foil and Backing Spring Construction

Combustion Chamber

The combustion chamber is the part of the engine where the fuel is mixed and burned with high pressure air coming from the compressor. The hot gases generated pass through the turbine section, where the thermal energy is converted into mechanical energy. Despite very high air flow rates, a combustor must contain and maintain stable combustion. To do so, combustors are carefully designed to first mix and ignite the air and fuel; they must then maintain combustion as the streams of fuel and air are varied to produce the desired load.

Recuperator

The recuperator is essentially a heat exchanger between the hot exhaust gas leaving the turbine and the relatively cool air leaving the compressor. Air typically leaves the compressor at a temperature range of about 150-200 ºC and recovers heat from the exhaust gases at 600-700 ºC. This increases the temperature of the working fluid entering the combustor, reducing the fuel needed to heat the working fluid to the required turbine inlet temperature. The fuel saved in this manner almost doubles the original fuel efficiency of the MGT. Unfortunately, the increased pressure drop of the recuperator can result in reduced power output, although the improved overall net performance often makes this an acceptable trade-off.

Figure 3-12: HiETA Technologies - MGT Recuperator

Electric Generator

The electric generator is part of the overall MGT package and is responsible for delivering the electrical output power of the system. It is typically coupled directly to the high-speed compressor-turbine shaft or through a gearbox at the conventional rotational speeds of 3,000 rpm or 3,600 rpm, depending on the desired output electrical frequency.

High-speed generators are typically paired with a set of power electronics to convert the high frequency AC electrical power to 50Hz or 60Hz outputs. This process is associated with an efficiency penalty of 5-10% due to the signal rectifying and inverting involved. However, for some single shaft machine designs, either a standard induction or synchronous generator can be used without the need for any power conditioning electronics.

At start-up, the electric generator operates as a motor to run the MGT.

CHP or CCHP Heat exchanger

If the MGT operates as a CHP or CCHP unit, the system includes a second heat exchanger that uses the remaining exhaust thermal energy after the recuperator. The available exhaust gas, typically at 300 ºC, provides energy that may be used for water and space heating, process heat application, or for cooling systems such as absorption chillers.

Figure 3-13: Mitis Heat Exchanger

## Comparison with Other Technologies

For both ground based power generation and micro CHP applications, there is competition from several alternative technologies. These technologies are briefly described below.

Internal Combustion Engines

Stirling Engines

Rankine Cycle Turbines

Pico Turbines

Fuel Cells

Internal Combustion Engines

Figure 3-14: Internal Combustion Engine

In an internal combustion engine (ICE), the combustion of fuel occurs with an oxidizer (generally air) in a combustion chamber, which is an integral part of the working fluid flow circuit. The expansion of the high-temperature and high-pressure gases produced by combustion applies direct force to some component of the engine. This force moves the component over a distance, transforming chemical energy into useful mechanical energy.

Stirling Engines

The Stirling engine is a heat engine that works by cyclic compression and expansion of air or other gases at different temperatures, such that there is a net conversion of heat energy into mechanical work. It is a closed-cycle heat engine with a permanently gaseous working fluid.

Figure 3-15: Stirling Engine

Figure 3-16: Steam turbine cycle

Rankine Cycle Turbines

Steam turbines utilise a Rankine cycle, which is an idealized thermodynamic cycle of a heat engine. It converts heat into mechanical work. The heat is provided from outside to a closed loop, where water is used as the working fluid.

.

FUEL CELLS

A fuel cell converts the chemical energy of a fuel into electricity through a chemical reaction of positively charged hydrogen ions with oxygen, or another oxidizing agent. Fuel cells can produce electricity continuously for as long as these inputs are supplied.

Figure 3-17: Scheme of a fuel cell

Even though all these systems can provide power outputs of relatively similar range, the different technologies do not necessary compete with each other; on the contrary, many of them may complement the others in CHP applications.

The different systems cover a wide range of thermal to electrical outputs, from very high percentage of heat generation for sterling engines to very high percentage of electrical power output for fuel cells. This inherently makes the systems appropriate to diverse applications, among which the demand for heat and power can be completely different.

As described previously, one of the most suitable markets for MGT-CHP systems is the lodging sector, which holds the largest ratio between thermal power requirements and electrical demand. These facilities require a significant amount of hot water for different services provided, such as swimming pools, bathrooms, laundries and kitchens. Another promising market for MGT-CHP projects may be found in healthcare facilities because of their high ratio between thermal and electricity needs in addition to their continuous demand for hot water to care for their lodged patients.

From the market point of view, the main competitor for the MGT is the ICE. Generally, the latter will have slightly higher electrical efficiency, approximately 30-34% compared to about 30% for a 100 kW MGT. However, as demonstrated in the OMES project [1], using MGTs brings along the following advantages:

- Lower maintenance expenses

- Lower primary exhaust emissions, especially NOx, CO and UHC

- Less space requirements

- Low vibration

- More multi-fuel possibilities

- Higher availability

## Technology Challenges

### Turbomachinery

#### State of the art

The turbomachinery components (e.g., compressor and turbine) are usually radial, a design approach that is simple, cost effective and efficient at this power range (typically up to 100 250 kW). Even though the compressor and turbine wheels constitute the core of the MGT concept, their respective cost is relatively low due to the fact that the designs originate from the automotive turbocharger field. In auxiliary power units, it is common for the turbine or compressor to be an axial type, but these units are more complex and are generally used in higher power machines. [7]

From an economic point of view, it is attractive to utilize existing MGT designs for biofuel-fired CHP systems. However, this poses challenges that are specific to the cycle configuration. For conventional cycles, the low calorific value of the biofuels requires the use of a larger fuel volumetric flow to achieve the design turbine inlet temperature. This will significantly affect the original matching with the compressor. Considering the common turbine chocking condition, the larger fuel flow rate would lead to a lower demand of air from the compressor and, in general, increase of compressor backpressure and surge margin reduction. One option to solve the turbine/compressor mismatch is to reduce the firing temperature or blow off the excess air from the compressor, both lead to reduction in the overall cycle efficiency. Another option is to increase the swallowing capacity of the expander, for example, by opening the nozzle guide vanes. This inevitably leads to change of incidence on the rotor blades and hence changes to performance. The third solution is replacing either the compressor or expander with a better-matched component.

#### Future Research Activities

If the objective is to strengthen the competitiveness of the European MGT industry, then the primary focus of future research activities should be on improving turbomachinery efficiency and costs. Even though the global energy efficiency of MGT projects are usually high due to the use of waste heat for cogeneration, the electrical efficiency is slightly lower than other competing technologies. As such, enhancing electrical fuel efficiency should be a focus of future research efforts. This target can be obtained by increasing the firing temperature in order to improve the Brayton cycle thermodynamic efficiency, or by means of an integrated and optimized design of MGT components (centrifugal compressor, radial inflow turbine, recuperator, etc.). Both these approaches are object of researches, even though they have different impact on machine manufacturing process. The first approach requires the use of advanced materials for the hot gas path components that are difficult to implement with radial turbomachines. On the other hand, component redesign with advanced optimization techniques allows for the use of current technologies and component manufacturing processes while still yielding tangible improvements to overall performance.

According to the ETN WG, future research activities on the turbomachinery should focus on the following topics:

Aerodynamic efficiency

Improvement of the aerodynamic efficiency using advanced fluid flow analysis and simulation.

  - Geometrical design optimization of impellers, blades, vanes, volutes etc. In [8] [9] [10] [11], an example is given of a project focused on systematically increasing MGT efficiency.

  - A specific aspect here are the small scale effects. Losses become increasingly large at low Reynolds numbers [12].

Tip clearance

Minimization of the tip clearance

  - This involves structural design issues, and also relates to rotor dynamics and bearings. Lessons learned may be taken from large aerospace axial gas turbine tip clearance control systems and through the use of new manufacturing techniques such as additive manufacturing.

Bearing losses

Reduction of bearing losses

  - This may include the development of advanced bearing solutions such as air bearings.

Other non-aerodynamic losses

Reduction of other non-aerodynamic loss effects, such as windage losses and thermal losses.

Cooling

Development of cooling concepts allowing higher turbine inlet temperatures for higher cycle efficiency. The use of additive manufacturing and other emerging technologies could potentially allow for the active cooling of both turbine wheels and housings leading to a significant increase of the turbine inlet temperature (TIT).

Cost minimisation

All these developments must be accompanied with efforts to minimise cost. Apart from military applications, competitive cost levels for MGTs will be essential for commercial success. For turbomachinery, the high-volume/low cost manufacturing technology from the automotive turbocharger industry may well be adopted.

### Combustion

#### State of the art

Direct or internal firing

In MGTs, two different types of combustors are used: tubular and annular combustion chambers.

Figure 3-18: Annular combustion chamber

Figure 3-19: Tubular combustion chamber

There exist three types of combustion technologies for gas turbines, namely:

- Diffusion flame – is the flame which is formed between the gas and oxidizer in the boundary layer. This kind of combustion of fuels is possible only when the mixing of substrates takes place by molecular or turbulent diffusion.

- Premixed flame - fuel is homogeneously mixed with air, and generally burn at lower combustion temperatures (600K below diffusion flames) in order to make low thermal NOx emissions that require high turbulence and other provisions to achieve flame stability.

- Catalytic combustion - It consists on combustion of fuel inside a porous ceramic medium, aiming to prevent the formation of NOx.

To stabilize the flame, a flow reversal pattern is typically created to ensure that part of the hot exhaust gases are recirculated and mixed with the incoming air and fuel. The most common way of introducing flow recirculation is with the use of swirlers. Swirl stabilized combustors are characterized by strong shear regions and high turbulence which allows for good mixing.

An alternative stabilization mechanism is jet stabilizing, which is characterised by the use of high momentum jets that are discharged through orifices into the combustion chamber. The axial high momentum jet flow provides strong recirculation in the combustion chamber and leads to an intense mixing of burnt gas with fresh fuel/air mixtures. To create an inner recirculation region, the orifices are usually arranged on a circular ring around the combustor. High flashback resistance is obtained through the absence of low velocity zones, which favours this concept for multi-fuel applications or very high combustor inlet temperatures.

Indirect or external firing

In an externally fired MGT, the combustor is a component separated from the balance of the turbomachinery. Heat produced by external combustion is exchanged with air coming from the compressor in a heat exchanger. Therefore, the efficiency of this system is limited by the operating temperature of the heat exchanger. This solution is particularly advantageous when burning biomass, coal or other solid fuels as this avoids the need to add a gasifier.

Figure 3-20: MGT indirectly fired, recuperated with recycled hot gases

As such, the system is similar to a Rankine cycle, but with higher efficiency. However, given the issues related to the slagging and fouling of the heat exchanger tubes, the indirect firing system has not yet achieved commercial success. Such systems have also been investigated for the firing of gas turbines with coal or other solid fuels.

Figure 3-21: MGT with external firing arrangements

Figure 3-22: The gasifier flaring the gas

Fuel Flexibility

Compared to piston engines, MGTs can be operated on low heating value fuels without engine derating. The combustion systems of MGTs can also be designed in such way that they can easily burn fuels with lower octane numbers (increased auto-ignition/detonation tendency) as well as gases with heavier hydrocarbon components (like Propane, Ethan, Butane, etc.) [13] [14] [15]. The same is true for fuels containing hydrogen (> 5% volume percent) [13] [16].

Most MGTs are typically operated with natural gas (NG) and biogas. Usually, a modification or entirely different design of the combustion system is required for different fuels. By altering the combustion systems to allow for the use of alternate fuel types, the potential range of fuels for gas turbines is large, and may include gaseous fuels like natural gas, hydrogen, biogas and syngas, to liquid fuels like gasoline, kerosene, and diesel fuel/distillate heating oil, and potentially other waste fuels like biomass.

Gaseous fuels

Natural gas (also sour gas), biogas (digester gas), landfill gas, manufactured gases, hydrogen, industrial waste gas, blast-furnace gas.

Liquid fuels

Heating oil, diesel/kerosene, nafta, LPG/NGL/LNG, liquid hydrocarbons, liquid biofuels (pure vegetable oil, biodiesel, bioethanol, biomethanol, glycerine or pyrolysis oil, VOCs (Volatile Organic Compounds)).

Solid fuels (biomass and waste (external combustion))

Wood, Agricultural waste, Municipal and industrial waste.

| Fuel | GCV (MJ/kg) |
| --- | --- |
| Biodiesel(from oilseed rape or recycled vegetable oil) | 37.27 |
| Veg. oil | 39 |
| Processed biogas | 22 |
| Agricultural waste (straw) | 15.8 |
| Animal waste | 18 |
| Waste food/fruits | 15 |
| Wood pellet/chips | 17.6 |
| Gas/diesel oil | 48 |
| Landfill gas | 22/m3 |
| Natural gas | 39/m3 |

Table 3-1: Calorific values of various fuels

Emissions

Burning fossil fuel releases the greenhouse gas (GHG) carbon dioxide (CO2) into the atmosphere, along with other air pollutants such as unburnt hydrocarbons (UHC), carbon monoxide (CO), nitrogen oxides (NOX), and sulphur oxides (SOX). The effects of these pollutants include, among others, global warming and acid rain.

Manufacturers of gas and liquid-fuelled MGTs and advanced turbine systems have bench test results showing that they beat current emission goals for nitrogen oxides (NOX) and other pollutants [17]. MGT systems are offering a competitive lower emission advantage in comparison to other CHP technologies.

MGTs typically use a lean premix combustion system to achieve low emission levels at full load conditions. Lean premix operation requires operating at a high air-fuel ratio within the primary combustion zone. The fuel is also thoroughly mixed with air before combustion. This premixing of air and fuel enables clean combustion to occur at a relatively low temperature [18]. Clean burning combustion is the key to both low emissions and highly durable recuperator designs. The most effective fossil fuel to minimize GHG emissions is natural gas since it yields less CO2 than other fossil fuels. Additionally, the wide availability of natural gas makes it the fuel choice for small businesses [19].

In an overview presented by B.L. Capehart [20] for MGTs between 25-500 kW for natural gas, hydrogen, propane, or diesel, the emissions of NOX are reported to be in the range of 9-50 ppm or less at baseload conditions.  For these systems, the total efficiency will vary with the configuration (e.g., un-recuperated 15%, recuperated 20-30%, and with heat recovery up to 85%).

|  | Capstone | Ansaldo | FlexEnergy | MTT |
| --- | --- | --- | --- | --- |
| NOx [@15% O2] | < 9 ppm | < 15 ppm | < 5 ppm | < 27 ppm (<10 ppm with FLOX) |
| CO [@15% O2] | < 10 ppm | < 15 ppm | < 5 ppm | < 50 ppm (<10 ppm with FLOX) |
| UHC [@15% O2] | < 9 ppm | N/A | < 5 ppm | N/A |

Table 3-2: Baseload emission for different micro gas turbine system

#### Future research activities

Fuel Flexibility

In general, all of the previously mentioned fuels can be used by a MGT to produce electric or shaft power and thermal power; however, the type and composition of the fuel does have a direct influence on flame stability efficiency, exhaust gas emissions, turbine corrosion, maintenance intervals and heat transfer processes. Due to the significant effort required when designing new combustion systems, the design of combustors capable of operating with fuels over a broad range of fuel types (multi-fuel combustors) is essential. This would increase the number of production units and lower production costs.

A promising near-term solution are MGTs connected to a biogas micro grid, which has gained significance with the support of public funding [21] [22]. However, the use of micro biogas grids requires CHP systems that can withstand varying fuel qualities, peak demands, or feeding-in natural gas to the local biogas grid to compensate for downtime at the fermentation plants. Moreover, if the fuel capability biogas combustors can be extended from very low energy fuels to higher energy fuels, like natural gas, then this would help to further reduce unit and maintenance costs while ensuring an easy exchange of combustors.

Another promising solution to reduce developmental efforts would be to design a MGT combustor capable of dual fuel operation, such as natural gas and heating oil. This would allow the same combustor to be used in both single fuel and multi-fuel applications, rather than developing separate designs for each fuel type.

Higher fuel flexibility in terms of operational range and fuel is required also in hybrid systems. An example is the hybrid power plant formed by the combination of a solid oxide fuel cell (SOFC) and a MGT. The system requires a combustion system able to oxidize the main fuel (natural gas or biogas, with a heating value up to 50MJ/kg) for start-up and shut down procedures and the SOFC off-gas (a syngas with a very low heating value of about 2MJ/kg) for base and part load conditions at very high combustor inlet temperatures up to 900°C.

A different hybrid example may be found by the coupling of a MGT with a solar system (solar dish / solar receiver). Such a system is an example of a “fuel replacing unit”. For proper operation, this system requires a MGT combustion system capable of stable combustion over a wide range of different air-fuel ratios and high combustor inlet temperatures to compensate the fluctuation in the solar heat input.

Another hybrid example could consist of a MGT combined with a “fuel producing system” like an electrolysis plant or a wood gasifier. In this instance, hydrogen produced by the electrolysis plant in times of excessive renewable electricity can be also used as fuel.

Non-conventional MGT layouts

Further combustion related research activities depend on specific requirements for non-conventional MGT layouts (e.g. exhaust gas recirculation, wet cycles, external combustion).

Exhaust gas recirculation is used to increase the water content of the combustion air to increase thermal efficiency by using the heat of condensation, or to increase the CO2 content of the exhaust gas to enhance CO2 capture and sequestration. To achieve a considerable increase in thermal efficiency, exhaust gas recirculation rates far above 50% should be achieved, which is beyond the capability of current conventional combustion systems.

In a wet cycle, the impact of the water injection on the combustion process has to be taken into account in the development of the combustor design.

An interesting evolution of MGT technology utilizes an external combustion system with the MGT. The development of a commercially viable Externally Fired Micro Gas Turbine (EFMGT) is still in progress, but when completed, could provide the typical advantages of gas turbines technology together with the exploitation of "carbon neutral" fuels.

Figure 3-23: Simplified sketch of a power station concept based on a wood gasifier with a micro gas turbine

Emission reduction

With regards to emissions, the targets listed below should be achieved in future research activities:

NOx < 5ppm (base load & part load 50%)

CO < 10 ppm (base load) & < 20 ppm part load 50%

UHC < 3 ppm (base load & part load 50%)

As a result of the significant progress achieved by industry and research groups, combustion in gas turbines for power generation is already relatively clean. However, the combustion systems of MGTs still show a large potential in emission reduction – even at the design point. In contrast to large gas turbines, MGT combustion is characterized by high combustor inlet temperatures leading to high adiabatic flame temperatures. Here, various MGTs demonstrated that single digit NOx values are achievable [18] [22]. On the other hand, the CO and UHC values at the design point (e.g. Capstone) and/or at part load conditions are rather high [18] [22]. Also, due to the new demands related to the integration of the renewable energies – primarily fuel and load flexibility – pollutants remain a main research issue at off-design or part load conditions. Under such conditions, one of the challenges is the reduction of CO while operating with the lower flame temperatures created by the higher air-fuel ratios of MGTs. This clearly indicates that further combustor design improvements are necessary.

The design effort required also increases in small MGTs with high turbine inlet temperatures and moderate pressure ratios using high temperature recuperators. In such systems, the combustor inlet temperature may also be above the self-ignition temperature of the fuel. This increases the risk of flash back and combustor damage. This makes the design of premixed combustion systems a challenge; especially in the case of conventional swirl stabilized combustors. Therefore, a high degree of fuel and air premixing is a must for many combustor designs to ensure low NOX emissions.

Jet stabilized combustion systems, like those based on the FLOX® concept, are an exception. Here, fuel is injected in the same direction as a high momentum air flow stream via a fuel nozzle. Air and fuel are partially premixed in a mixing section before the mixture enters the combustion chamber. The premixing is required to decrease the otherwise long combustion zone. The high jet velocity generates a strong inner recirculation zone which dilutes the incoming fresh gas with hot exhaust gas. This leads to a homogeneous temperature distribution without hot spots, which is essential for low NOX emissions. Due to the high jet velocity, the risk for flashback is significantly reduced, even when pure hydrogen is used as fuel. The development of FLOX® based combustors for MGTs just started in recent years within DLR (e.g. for natural gas, wood gas or biogas) and demonstrated the potential of this combustion concept [14] [15] [22].

Combustion of the new fuels listed above can lead impact pollutant formation. Therefore, optimal operating conditions for MGT combustors have to be identified in an approach using appropriate numerical tools and detailed and experimentally validated information on the underlying physics and chemistry while at the same time observing system requirements. This is especially true for the mixing process between the fuel and oxidant since mixture preparation greatly affects the turbulence dominated flame characteristics. Since Large Eddy Simulation (LES) has contributed largely to the understanding of the very complex turbulence-combustion interaction process, modelling the unsteady behaviour of a lean premixed combustor using the LES methodology in conjunction with combustion models should be investigated.

### Materials

#### State of the art

Recuperator

The recuperator is one of the critical components in MGT systems and is responsible for a significant percentage of the overall efficiency.

Recuperators are classified by their method of construction into three basic types: shell-and-tube, plate-fin, and primary surface recuperator (PSR) [23] [24] [25]. All of these high temperature heat transfer systems have a common requirement for high materials performance.

Figure 3-24 – Annular PSR recuperator

Since the thermal efficiency of a recuperator generally increases as the air cell wall thickness decreases, thinner foils and alloys with good high temperature strength are desired. In addition, the alloy foils must be able to withstand extreme deformation during the manufacturing process of the air cells. Thus, fine-grained alloy foils with high creep strength at the maximum operating temperature are required. Most turbine recuperators currently in production operate at a maximum temperature ranging from 600°C to about 750°C [26].

The other property that the recuperator materials must provide is an excellent oxidation resistance. As a result, alloy systems that could be considered for this duty include: austenitic stainless steels, ferritic steels (e.g. FeCrAlY alloys and their ODS variants) and nickel-based alloys (with high chromium and/or aluminium contents). An example alloy used for recuperator applications, in particular by ANSALDO, is MA 253. This is an austenitic chromium nickel steel alloyed with nitrogen and rare earth metals. This grade is characterized by:

- High creep strength

- Very good resistance to isothermal and cyclic oxidation

- Good structural stability at high temperatures

- Good weldability

- Maximum operating temperature of approximately 1150°C (2100°F).

Rotor and Stator for Turbomachinery

The state-of-the art rotor materials are Ni-based superalloys, such as MAR-M-247 [28] used by ANSALDO (MAR-M is a registered trademark of Martin Marietta). Mar-M-247 is a polycrystalline cast nickel base superalloy. It is commonly produced using directional solidification techniques to improve creep rupture strength. It has high temperature strength, corrosion and oxidation resistance. Additionally, HiETA Technologies is currently developing the capability to use Additive Manufacturing with both CM247LC and Haynes 282 for use in high temperature turbomachinery and recuperators.  This may also enable the production of turbine wheels for increased operating temperatures (potentially 1200ºC or more).

For MGTs stator, Alloy 713C is an example used in the ANSALDO engine. It is a precipitation hardenable nickel-chromium base cast alloy, with excellent strength properties up to 1800°F (982°C). This alloy is characterised by good castability, remarkable resistance to oxidation and thermal fatigue, and outstanding structural stability [27].

#### Future Research Activities

The future of materials for MGT is currently oriented in two directions: metallic materials on one side and ceramic materials on the other. While metallic materials are currently the only choice in the market, and a proven solution, ceramic materials have the potential for higher speed and firing temperatures for higher overall fuel efficiency.

Ceramic gas turbine development activity has been ongoing since the 1950s, heavily supported by governments in the United States, Japan, the countries of the European Union, and those of the former Soviet Union. Primary drivers for these programs were promises of improved high temperature durability (compared to superalloys), improved engine performance, light weight, and independence from strategic elements like Co, Cr, and Ni. Rig and engine testing during the early development, typically for up to several hundreds of hours, showed good potential for performance improvements with ceramics. However, long-term engine tests that started in the 1990s, conducted for many thousands of hours at field demonstration sites, revealed shortcomings (e.g. material resistance) that severely dampened the enthusiasm of gas turbine designers for ceramics. [29]

Even with decades of research and large investments, there has been no breakthrough for ceramic materials sufficient to overcome its main shortcomings. New technological improvements, such as additive manufacturing, could improve the cooling of components and ease material strains, potentially solving some of the major issues found for ceramic materials.

Recuperators

In developing heat exchangers for MGT systems, it is necessary to consider that they have to comply with space and layout restrictions that markedly affect the conceptual design of the recuperator. In addition, they have to withstand the constant temperature differentials across the surface area, and have to provide an operating life of several thousand hours with hundreds of start-up/stop cycles. It is also very important to balance the need for higher performance and more durable materials with the need to make them as cost effective as possible and reduce pressure losses [30].

Metallic Materials for Recuperators

During last 10-15 years, intensive research activity has been carried out to identify and evaluate candidate alloys that could meet the performance requirements discussed above. In particular, a significant effort on this subject has been made by the Oak Ridge National Laboratory (ORNL) with support by the US Department of Energy (DOE) under its Advanced Microturbine Program [30].

The higher performing (and more expensive) alloys can be divided into two different groups [25]:

- Alloys comparable with 347 stainless steel, such as modified Alloy 803, Alloy 602 CA, Haynes HR120 and Haynes HR230

- Alloys considerably stronger than 347 SS, such as Alloy 625, Haynes HR214, Hastelloy X and Plansee alloy PM2000 (ODS alloy).

In this classification alloy 740 represents a sort of dividing line.

The potential benefits of additive manufacturing may soon be realized with higher performing alloys. For example, Alloys 625 and 718 are now available as additive manufactured materials, and alloys 282 and 247 are in development by HiETA Technologies for high temperature recuperator applications, offering high strength and corrosion resistance at elevated temperatures (1050°C or more).

Composite Materials for Recuperators

Solid materials holding promise for use in heat exchangers can generally be divided into four categories: polymers, metals, ceramics and carbonaceous materials. In many heat exchanger applications, these materials perform satisfactorily in their unmodified or non-reinforced form. However, in some applications, more advanced structural materials are needed. These materials need to be stronger, stiffer, lighter in weight, and more resistant to hostile environments.

Composite ceramic materials offer engineers the ability to create a limitless number of new material systems with unique properties that cannot be obtained using a single monolithic material. This approach to construction holds tremendous promise for future heat exchanger designs. Rather than selecting a single material, multiple materials may be selected and then tailored to meet the specific requirements of an application. Composite materials are constructed of two or more materials, commonly referred to as constituents, and have characteristics derived from the individual constituents. The constituent that is continuous and often present in the greater quantity is termed the matrix. The second constituent is referred to as the reinforcing phase, or reinforcement, as it enhances/reinforces the properties of the matrix. By combining matrices with thermally conductive reinforcements, such as special carbon fibres, SiC particles and diamond particles, it is possible to create new materials with high thermal conductivities and a wide range of coefficients of thermal expansion (CTEs) [31]. With respect to high efficiency MGT recuperators, available literature suggests that SiC may be best option for the manufacturing of this component.

Rotor and Stator for Turbomachinery

When burning biofuels in a MGT, both the rotor and stator are confronted with a harsher environment as the composition of the combustion products are more aggressive and accelerate the corrosion process. The problem is common to both metallic and ceramic rotors. The simplest and common choice to overcome the corrosion issues is to add or modify the material coatings used instead of modifying the base alloy.

If the MGT is running with a solar energy source, the temperatures achieved in such systems are comparatively low (800ºC). The factor limiting the maximum temperature is currently the receiver technology. In this case, there is no need to use ceramic materials to increase efficiency as high temperatures are not reachable. Additionally, corrosion issues are minor due to the low temperatures and the clean working fluid (air without burnt fuel). However, if a hybrid fuel-solar system is considered in order to make it a dispatchable-energy unit, corrosion issue would be the same as in any other MGT.

Metallic Materials for Rotor and Stator

Cast superalloys, providing an outstanding balance of high temperature strength, fatigue resistance, oxidation resistance and coating performance and that can be manufactured to high tolerances in complex configurations, are commonly used in the most demanding applications of aero and industrial gas turbines, and their use is expanding also to smaller MGT engines. Therefore, during last few years, the application of cast Ni-base superalloys for use in small turbines has been evaluated by Cannon-Muskegon Corp [29].

A range of alloys has been considered encompassing nickel, iron and cobalt alloys that can be utilized structurally at operating temperatures of up to 900°C. They include conventionally cast, equiaxial (EQ) alloys, directionally solidified (DS) and the more advanced single crystal alloys (SX).

The use of light metallic alloys, such as titanium aluminide, for the turbine impellers could be beneficial in some MGT applications. A light-weight turbine impeller could improve the dynamic stability of the rotor assembly in applications over a wide range of operating speeds. One example is the MGT for Concentrated Solar Power, whose MGT operates over a wide speed range due to the variation in received solar power. Gamma type titanium aluminide (-TiAl) is the main candidate in this range of alloys since they have interesting mechanical and thermal properties at high temperatures up to 950°C. There have also been significant advancements in manufacturing process for turbomachinery components with this range of alloys using Additive Manufacturing.

Ceramic Materials for Rotor and Stator

Silicon nitride has traditionally been the ceramic material of choice for the manufacturing of rotor components (including rotating and static parts). Most of the silicon nitride investigated for this kind of application are materials sintered with the addition of yttria and alumina, but the material considered to be the most resistant, from a mechanical point-of-view, is a silicon nitride produced by Kyocera. Silicon nitride from Kyocera incorporates Lu compounds, and are identified as either SN281 or SN282 (based on their application for rotating or static parts, respectively) depending on the sintering procedure applied for manufacturing.

Two prototype micro-rotors have been produced and largely characterised at ORNL (as part of a U.S. DOE supported program on distributed energy): one rotor was manufactured for an Ingersoll Rand machine project while the other one was manufactured by UTRC for a machine project developed in agreement with Pratt & Whitney Canada. The following figures show micro-rotor prototypes [32].

Table 3-3: MGT's rotor prototypes

### Recuperator

Different recuperator technologies have been developed, tested and used over the last decades.  This section tends to sum-up and review some of them.

#### State of the Art

Different recuperator technologies have been developed, tested and used over the last decades.  This paragraph tends to sum-up and review them:

- ACTE: annular type recuperator, primary surface, counter-flow. Millimetric hydraulic diameter, washboard corrugated pattern, local pressure retention.  Fully laser and TIG welded.  Metallic (typically 3xx, austenitic SS series).  ACTE cores are obtained by the coiling of a pair of patterned sheets.  Air and gas flow parallel to the coiling axis.  Headers are welded on each side of the cylinder to distribute and collect compressed air radially.

- Bosal: Primary surface, millimetric hydraulic diameter, counter-flow, inclined corrugated pattern stimulating micro-turbulences by shear layer to improve heat transfer. Fully stainless steel high alloyed foil typical 3xx applied in series, and also demonstrated with creep resistant Inconel and alumina forming grades. Rectangular type cells, fully laser-welded, stacked in rectangular box type core with easy modular sizing in line with customer specifications based on number of cells. Progressive embedding of thin foils (thickness hundred of microns) up to manifolds with thickness of multiple millimetres. Designed for minimal thermal bridges to have 90% effectiveness. Manifold design with CFD-verified flow uniformity. Cold start-stops resistant design and proven in accelerated tests. Range covering 10-250kWe devices. European Pressure Equipment Directive certified unit according PED 2014/68/EU for serial production. Design accumulated already more than 3 million hours in the field.

- Capstone: Trapezoidal welded air cells, stacked in an annular way to achieve a annular, primary surface, counter-flow heat exchanger. Millimetric hydraulic diameter, wavy channels. Metallic (typically 3xx, austenitic SS, HR120 or Inconel series).  Flow parallel to the annular axis.  Compressed air distribution via the internal diameter.

- HiETA: Additive manufactured, typically Inconel, recuperators featuring optimised secondary surfaces and integrated manifolds/ducts. Recuperators can be annular, rectangular or any other shape, and due to highly effective secondary surface features significantly smaller than conventionally manufacture alternatives, making them cost effective also.

- MTU: Shell & tube heat exchanger.  Tube with an elliptical cross section.  Tube for instance bended in a U configuration to achieve a counter-flow arrangement.  Tubes ends brazed on 2 end plates to distribute and collect compressed air. Metallic (typically 3xx, austenitic SS or Inconel series).

- Solar: plate and fins (primary + secondary surface).  Stack of plates ending in a rectangular shaped recuperator.  Air distributor and collector welded on the core.  Counter-flow arrangement. Millimetric hydraulic diameter.  Metallic (typically 3xx, austenitic SS series).

- ToyoRadiator: plate and fins (primary + secondary surface).  Stack of plates ending in a rectangular shaped recuperator.  Air distributor and collector welded on the core.  Counterflow arrangement. Millimetric hydraulic diameter.  Metallic (typically 3xx, austenitic SS series).

#### Future research activities

A gas turbine recuperator is a gas-to-gas heat exchanger, typically counter flow, for recovering gas turbine exhaust heat for pre-heating combustor entry air in order to save fuel. In terms of heat exchanger design, the combination of requirements imposed by the gas turbine cycle makes successful development of a recuperator an extraordinary tough challenge. These requirements include:

- High effectiveness (typically >80%).

- Low pressure losses (typically not more than a few percent (<2-4%) for both hot and cold flow paths. Note that pressure loss and effectiveness are often related, with high effectiveness typically obtained at the expense of high pressure loss for the same volume.

- Resistance to high temperatures (steady state, creep life and corrosion resistance). Depending on the turbine inlet temperature and turbine efficiencies, the general ranges for the maximum turbine inlet temperature, and the common alloys used are:

- With high cycle pressure ratios (>5), usually 650-700 ˚C (stainless steels).

- Low cycle pressure ratios (<4) >750˚C (advanced/nickel based high temperature alloys).

- Resistance to thermal shock and large temperature gradients in the structure (low cycle fatigue life).

- Large pressure difference between hot and cold flow. For example, with a cycle pressure ratio of 7, the pressure difference will be 6 bar, resulting in significant structural loads in the heat exchanger matrix.

- Compact / low weight design.

- Minimal heat loss (insulation).

- Affordable costs:

- Minimal use of expensive materials.

- Low manufacturing costs.

- Recuperator operation in mobile systems

In order to improve the know-how associated to recuperators in Europe, different work areas have been identified. Those are

- WP1 Thermodynamic optimization

- WP2 Gas composition and anti-fouling channels geometries

- WP3 Materials

- WP4 Cost minimization

Thermodynamic optimization

The recuperator parameters that mainly affect the overall efficiency of the MGT are the effectiveness and the pressure losses. If the effectiveness increases (maintaining the same heat transfer coefficient), the exchange surface must grow, resulting in a larger recuperator. For a constant exchange area, the heat transfer coefficient can be increased with more turbulent flows (and/or with secondary flow structures), but this increased pressure losses.

This means that the geometry of the exchange surfaces must be optimized in order to find the best compromise (in terms of the overall machine efficiency) between heat transfer, compactness and pressure losses.

3D-trade-off regarding recuperator effectiveness, backpressure and cost.

- Literature: collection of gas-to-gas heat transfer coefficient and pressure drops laws.

- Micro-channel CFD analysis to validate the laws in the recuperator conditions

- Local optima - What could be local optima within this 3D-space?

- Global optima - Is there a global optimum feasible? Can a perpetuum mobile be reached?

- Matching Recuperator systems to the application.

Gas composition and anti-fouling channels geometries

Compatibility of the recuperator with the turbine fuel flexibility.

- Exhaust gases characterization - Physical properties of the gas: Cp values, viscosity, particles characterization, condensation behaviour, etc.

- Sensitivity of the recuperator regarding contamination and performance loss (effectiveness and pressure drop) due to exhaust impurities. Anti-fouling methods (description, test: pyrolysis, vapour, etc.).

- CFD analysis to validate fouling.

- Possibility of Cleaning of recuperator systems

Cost minimization

Another issue related to the recuperator surface is the manufacturing process: the geometry of the heat exchanger and the assembly process of its parts must be compatible with automatic machining/assembling techniques. The primary surface type currently appears to be the best solution from the point-of-view of cost and reliability.

Cost reduction of the recuperator is achievable implementing the following actions:

- Determine the potential effects on cost reduction by manufacturing designs at high volume that are based on the following:

- Modularity

- Standardization

- Compactness

- Automation in serial production

- Determine the possibilities of cost reduction by process and material selection.

- Identify total value cost reduction possibilities by advanced integration with a specific engine.

- Integration of recuperator systems in the process.

- Determination of recuperator design parameters that influence emissions, and how they may be used for emissions reduction.

### System Integration

#### State of The Art

Currently, the system layout for commercial MGTs with the largest number of machines is based on a recuperated Brayton cycle. However, various component integration activities are currently under development to combine renewable energy sources with MGT technologies. All the innovative solutions proposed to improve MGT performance are just related to research activities because they are far from commercial level with many cost and technological issues remaining to solve. At the moment, the following innovative system layouts are under analysis from both a theoretical and experimental point of view:

- Hybrid Cycles

  - Integration with high temperature fuel cells

  - Integration with Concentrated Solar Power (CSP)

- Integrated Cycles

  - Integration with energy storage technology

  - Integration with bottoming cycles

- Non-Conventional Cycles

  - Wet cycles (especially micro Humid Air Cycle (mHAT)  plants)

  - Inverted Brayton Cycle

Even if prototype devices were successfully developed, the following component integration issues remain unsolved: compressor instability, costs related to high temperature components, control system development, additional constraints due to sensible components (e.g. the SOFC), exceptional complexity level, reliability, etc.

#### Future Research Activities

As described previously, current development for power generation is following two main trends: towards smaller distributed units and plant integration into wider energy systems. Wider energy systems consist of an integration of various energy sources or plants with a clear trend towards high efficiency, renewable energy and utilisation of low energy flows, such as coupling electrical and thermal systems (e.g. district heating). In this context, MGTs are positively competing against internal combustion engines in terms of low maintenance, noise and emissions. Furthermore, they are interesting devices for development of advanced plants, such as hybrid systems based on fuel cell technology.

MGT designs currently available offer a compact and integrated design for all its components in order to improve the MGT efficiency and operation in conventional recuperated Brayton cycle. However, this acts against the ability of the MGT to be integrated or hybridised with other technologies, making it more complex and expensive to open and modify the cycle. Therefore, there is a particular need to design MGTs for integration with other technologies in order to increase the flexibility and ease of MGT integration with other systems.

As a consequence, MGTs and their cycles need further development towards:

•	Higher electrical efficiency;

•	Increased flexibility for integration with other systems;

•	Increased flexibility towards the utilization of various sources of energy.

Therefore, future development activities should consider the following three aspects:

- Improvement of current cycles and new advanced cycles;

- Development of the necessary technologies to allow the design of advanced and new cycles;

- Design of MGTs according the needs of the new processes and their integration into other cycles.

The different system configurations that require development for the advancement of the MGT technology fall within three categories: Hybrid Cycles, Integrated Cycles and Non-Conventional Cycles. Hybrid Systems are configurations where the traditional MGT cycle is opened to include a different technology in-between. Integrated Systems refer to cycles where the MGT can still be considered as a single unit that is connected with other cycles or technologies. Non-Conventional Cycles include cycles strictly for the MGT technology that are different from the Brayton and recuperated Brayton cycle.

Hybrid Cycles

Important issues have to be analysed for MGTs in hybrid systems, such as cycle layout (including MGT and component optimisation), system dynamic aspects affecting the machine (especially surge problems due to the connection with a large volume), MGT control system issues to manage all the additional constraint problems, and other interaction aspects with the other technologies (e.g. fuel cell, CSP).

Unexpected issues might arise when integrating a MGT with other equipment due to the exception of gas turbines from the pressure equipment directive (directive 97/23/EC under 3.10). Especially when the MGT is integrated with a large volume technology such as a fuel cell, a humidification tower for a wet cycle is a conflict rising based on the fact that the volume and connected components need to fulfil the requirements of 97/23/EC. Due to this conflict, it might it be necessary to add or integrate additional components, such as additional fast shutoff and/or blow off valves, additional pressure boundaries, different and certified elements in the fuel system, etc.. As such, this conflict might result in significantly increased costs and impact the techno-economical feasibility of the concept.

MGT-SOFC Cycle

Due to the importance of future opportunities (e.g., efficiencies greater than 60% in small scale units, low/near-zero emissions, and the potential for growth in the distributed generation marketplace), special attention should be placed on Solid Oxide Fuel Cell (SOFC) based hybrid systems. Even if different layouts are possible, the plant scheme based on a pressurized SOFC seems to be the most promising for efficiency point of view.

Figure 3-25: Generic plant layout for a SOFC base hybrid system

As shown in Figure 3-25, the system is based on the coupling of a SOFC stack with a MGT equipped with a recuperator (other configurations are possible without the recuperator, including cathodic recirculation). Air is compressed and preheated upstream of the cathodic side of the fuel cell. On the anodic side, fuel is mixed with a recirculated flow containing steam for the reforming process that produces a hydrogen rich fuel. These are performed internally inside the anodic ducts or just upstream of the fuel cell inlet. The un-oxidized fuel in the SOFC ducts reacts with the oxygen in the cathodic exhaust using an Off-Gas Burner (OGB) located upstream of the turbine (or in the cathodic recirculation line, if present).

Next, the MGT exhaust flow is used in the recuperator to pre-heat the fresh air for the SOFC. Moreover, co-generation plants may include an additional heat exchanger to produce hot water (or steam) for thermal loads from the remaining energy in the MGT exhaust. Finally, the power generated by the SOFC stack is converted from DC to AC using an inverter, while the power from the machine alternator is converted from high frequency AC power to standard AC power using the MGT system’s power electronics.

Even though the overall system concept is well known, these hybrid plants are not ready for commercialization due to various unresolved issues, including high cost, low reliability, issues related to the SOFC coupling with gas turbine technology, and control system aspects. Compared to prototypes working with natural gas, a complete re-design of the fuel system is also required for the anodic recirculation line. Moreover, operation with a large amount of inert gas in the fuel duct can produce additional surge risks that must be carefully evaluated and prevented. Thus, further research activities are necessary for both natural gas based solutions and biofuel/syngas plants.

MGT-CSP Cycle

Though the MGT-CSP cycle was discussed earlier in this document, it is important to add that the hybridization should ideally include the use of biofuels. This will significantly improve the availability of the plant. Furthermore, the fuel flexibility of the a MGT may make this the easiest and most efficient technology to utilize in terms of solar/other fuel hybridization, though a significant level of work may be required to develop the combustion chamber/solar receiver section of the cycle.

Figure 3-26: OMSoP plant configuration

Integrated Cycles

Integration with Bottoming Cycles

MGT may be integrated with bottoming cycles (e.g. ORC (Organic Rankine Cycle) or others) to increase electrical efficiency.

Energy Storage Integration *Renewable Energy Source*

The combination of a MGT with an energy storage technology into an overall system that is well suited for electrical and/or thermal loads that vary with the time of day. This cycle also supports the integration of fluctuating renewable energy sources, such as equipping CSP plants with high temperature energy storage systems. There are numerous applications of MGTs in co-generation plants and smart grid applications, including the generation of chilled water with absorption chillers. Even though this point mainly relates to the integration of existing technologies, optimisation of the whole system is essential for efficient management.

Non-Conventional Cycles

Wet Cycles

Wet cycles, which are considered advanced cycles, are processes with extraordinary high water content in the work fluid (e.g. humid air turbine, TopCycle etc.). A few general aspects of these cycles that would benefit from R&D activities are as follows:

- Combustion operation, including stability and surge margin, should be improved for applications utilizing water injection.

- The challenges when connecting the MGT to bigger volume technologies for the purpose of humidification and the resulting change in transient behavior as well as during start-up and shutdown operations need to be considered in close connection with the development of wet cycles.

- Topics related to water recovery at the MGT discharge duct may be particularly important for applications with limited water sources.

- The impact of water injection on MGT components, such as lifetime and performance.

- The humidification of MGT combustion air to increase the overall electrical efficiency during periods of low heat demand.

Inverted Brayton Cycle

Inverted Brayton cycle (IBC) for very small units (less than 2 kWe, no turbochargers available) or for small units (up to 30/50kWe) using very low caloric fuels containing hydrogen (e.g. wood gas). This cycle eliminates the high power needed for the fuel compressor and the technical and economic problem of compressing hydrogen fuels.

MGT Design for New Processes

Most current designs utilize a compact MGT with closely integrated and connected components (compressor, combustor, turbine, recuperator) which makes it challenging to integrate them into other processes. As a result, MGT designs differ significantly from systems designed for mechanical integration with other equipment (e.g. turbochargers).  Therefore, future MGT research activities should focus on the following:

- Provide the ability to match different compressor and turbine specifications (e.g., for various mass flow differences);

- Design recuperators that are more resilient to changes in flow composition and load. Current recuperators are optimised for “normal” MGT operation. This makes it difficult to ensure optimised operation when, for example, injecting water into the combustion air. More resilient recuperators may introduce a small efficiency penalty when working in ‘normal’ conditions, but could better adapt to changes in MGT load and flow composition to ensure a higher overall efficiency;

- Incorporate specific connection points to other components (flange dimensions, positions and forms);

- Develop specific MGT operating profiles that are optimized for different load profiles to maximize overall efficiency. For example, one profile may be specific for peak load efficiency (i.e. base-load operation), while another profile may be optimised for a continuously variable load (compromising peak load efficiency for the benefit of overall efficiency).

A new MGT design intended for integration with other systems must also incorporate the following features and activities:

- A modular and open design:

  - Allows the integration of other heat sources (e.g. CSP, high temperature waste heat) while still keeping the combustor;

  - Allows Easy exchange of the combustor for another version better suited to a different fuel or complementary firing;

  - Allows incorporation of design aspects that allow the exhaust heat to be used for various other purposes;

  - Allows incorporation of  components that allow a high flexibility for external connections (e.g. flanges or tee joints);

  - Allows the adjustment of MGT performance to better match the specifications required by advanced cycles, such as hybrid systems based on fuel cells.

- A more open control system:

  - Enables integration into a different system or cycle;

  - Allows additional signal I/O;

  - Allows MGT operational control to be determined by external controllers from integrated systems (e.g. fuel cells, water injection unit, EGR);

  - Allows safety relevant signals to protect connected components;

  - Provides for the future addition and control of new hardware and functionality (e.g. second combustor, additional valves etc.);

  - Allows MGT interconnection with other controllers in the energy system as either a master or a slave;

  - Enables the implementation of innovative control approaches, such as Model Predictive Control based solutions;

  - Allow for easy integration with external and/or additional diagnostic tools.

- Techno-economic analysis tools:

  - Enables validation of all new system/cycle developments in a future energy system;

  - Enables evaluation of the potential technology cost of a system in terms of LCOE.

Opportunities exist to utilise new and emerging manufacturing techniques such as Additive Manufacturing to improve the integration of components for reduced losses, increased thermal efficiency and reduced weight/cost, and to allow multiple design variants to be generated without tooling costs and setup times.

## International Developments

This paragraph is intended to the main, but not exhaustive, list of EU co-funded MGT projects.

| PROJECT | Description |
| --- | --- |
| BIO-HYPP | Biogas-fired Combined Hybrid Heat and Power Plant The Bio-HyPP project aims to develop a full-scale technology demonstrator of a hybrid power plant system – a combination of solid oxide fuel cells (SOFC) and a MGT – using biogas as main fuel in lab environment. |
| BIOMGT | BIOMGT The BIO_MGT project aimed to demonstrate the technical feasibility and to evaluate the performance of a small polygeneration unit based on a MGT fed by woodchips. |
| BIOTURBINE | Opportunities for biofuel-burning Microturbines in the European Decentralised-generation Market The aim of the project was to assess the technical feasibility and the market potential of microturbines that run on liquid biofuels (bioturbines) for power and heating applications (CHP). |
| CAME-GT | Thematic network for cleaner and more efficient gas turbines The objective of this Thematic Network (TM) was to coordinate research, technological development and demonstration (RTD) projects in industrial gas turbines, including projects from FPIV and FPV covering fossil fuels and biomass; and gas turbines in CHP applications and combined cycles. |
| CHEP | Research and development of high efficiency components for an intercooled, recuperated CHP gas turbine for combined heat and efficient power The project aimed to the initial development phase of gas turbine cogeneration unit capable of meeting current market requirements in terms of power output, efficiency, reliability and cost. |
| ELEP | European Local Electricity Production ELEP set out to support the use of DG in Europe by removing the regulatory and practical barriers currently restricting its use and by developing a roadmap and timeline for its deployment. The project set out to identify and address the barriers affecting DG use, and to propose solutions and methods by which the barriers could be minimised through policy and legislation. Another key objective was the establishment of detailed EU policy guidelines on connection charging, ownership of equipment, net metering and feed-in tariffs. |
| E-TRIGEN | Tri-generation and integrated energy services in the South of Europe and Brazil The project demonstrated an innovative integration of three technologies: micro turbine, hot water fired absorption chillier, and ice storage thermal system. The aim was to demonstrate the main benefits resulting from the activity of Energy Services Companies while using the micro tri-generation system and a flexible financing mechanism. |
| IM-SOFC-GT | Integrated Modelling study of FC/GT hybrids The main objective of the project was to develop the capability to assess the performance of Fuel Cell (FC) and Gas Turbine (GT) hybrids using closely integrated system and stack models and specific performance requirements. |
| IRMATECH | Integrated Researches on MAterials, TECHnologies and processes to enhance MCFC in a sustainable development The IRMATECH project aimed at several industrial objectives: - Cost reduction of a MCFC plant from about 8000 to about 1000 €/kW in the next 10 years through (a) reducing costs related to materials and manufacturing processes of 50%-70%, and (b) increasing the compactness of a MCFC by 40% - Increase the service life from 20000 hours to 40000 hours - Minimisation of the environmental impact and energy required for manufacturing. These three major objectives will be achieved by working on the following: - Fuel Cell System: reduced manufacturing costs and increased life-time; - Balance of plant: multifuel capability - one unique reactor for all the fuels; - Integrated system analysis. |
| OMES | Optimised Microturbine Energy Systems The project showed that the technology is functional and reliable. Work is still required to reduce costs before the micro turbine can be fully commercialized. The original goals were to achieve ≥30% power efficiency and an overall efficiency ≥80% (ref. LCV) during full load operation. |
| OMSoP | Optimised Microturbine Solar Power System The overall objective of this project was to provide and demonstrate technical solutions for the use of state-of-the-art concentrated solar power systems (CSP) coupled to micro-gas turbines (MGT) to produce electricity. The intent is to develop a modular system capable of producing electricity in the range of 3-10 kW for domestic and small commercial applications. |
| SLUDGE2ENERGY | A way to energy-autarkic operation of sewage treatment plants The aim of the SLUDGE2ENERGY project was to demonstrate the decentralised reuse of sewage sludge in an efficient small-scale heat and power generation plant on the premises of the wastewater treatment plant (WWTP). The innovative sludge processing technique was intended for market introduction. The energy self-sufficient plant would reduce the amount of sewage sludge for disposal to 1/8 of the dewatered sludge. |
| MOCAMI | Innovative cost-effective hybrid system based on integration of a MCFC and a gas turbine for high efficiency dispersed CHP generation The project aimed at developing and demonstrating a small-sized hybrid system combining MCFC technology with MGT technology. The development of such a small-sized hybrid system will lower production costs through the development of new and simpler processes with better quality control and a higher component production yields. |
| SOLHYCO | Solar-Hybrid Power and Cogeneration Plants The scientific and technological objective of the SOLHYCO project was to develop and test a highly efficient, reliable, and economic solar-hybrid cogeneration system based on a 100 kW microturbine capable of parallel operation with varying contributions of solar power input and fuel. A new receiver concept, based on an innovative receiver tube configuration, shall improve performance and reduce system cost. Enhancing the combustion system to multi-fuel capability, including bio-fuels, will allow operation with up to 100 % renewable energy sources. |

# Expected Impacts

## Energy Saving

Energy savings is one of the key European policy goals for the near term. In this context, the MGT may be seen as a significant contributor towards achieving this target.

In an EU context, where the demand for heating power amounts to 50% of EU energy consumption, and where 45% of that energy consumption is used in residential sector, MGT CHP systems can easily justify their place in the future energy sector.

With the ability to attain overall efficiencies above 90% (electrical efficiency of more than 30% with the heat exchanger), MGTs with micro-CHP units meet the demand for heating, space heating and/or hot water (and potentially cooling) in buildings, while providing electricity to replace or supplement the grid supply. This would diverge from conventional power generation, where electrical output is produced in power stations of electrical efficiencies typically between 35% and 40%. On the other hand, thermal outputs are generated locally with boilers of around 80% efficiency. Currently, there are more than 100 million boilers installed in EU homes.

The study conducted within the CODE 2 project shows that micro-CHP systems that can exceed 80% efficiency are also able to save on energy losses related to long distance electricity (8-10% losses) and heat (10-15% losses) transportation. In this context, as shown in figure below, for a demand of 260 units (160 thermal and 100 electrical) the conventional generation methods would require 465 units of fuel to be consumed. However, a CHP system could deliver both outputs for just 325 units of fuel, resulting in a potential 30% energy savings.

Figure 4-1: Comparison energy losses micro-CHP and conventional systems

Figure 4-2: micro-CHP systems for residential

Depending on the regulatory arrangements in place, the electricity produced by micro-CHPs could be sold to the local supply network. The heat generated could be used on-site (combined with, or replacing gas fired boilers) and/or supplied to other nearby homes through a district heating infrastructure. MGT with micro-CHP systems can also provide cooling through the use of absorption chillers that utilize heat as their energy source (i.e., Combined Cooling, Heating and Power). In this way, end-users from different sectors (including multi-family buildings, commercial, and industrial applications) become partners sharing responsibility for a greener and more sustainable energy supply.

A micro-CHP system is also a controllable Distributed Generation (DG) solution that can empower consumers by enabling them to produce their own electricity and heat, taking control of their energy bills (i.e., becoming active participants in the energy market). Also, as the viability of carbon capture and storage (CCS) solutions remain in doubt, micro-CHP systems may be able to play a leading role in meeting domestic decarbonisation targets.

In summary, micro-CHP systems can deliver important benefits to energy consumers as well as the wider energy system, and assist the EU with reaching its energy and climate objectives by providing the following:

- Energy savings between 25%-44% (depending on the size of the MGT) compared to a traditional system of separate electricity and thermal energy generation,

- Savings on total energy costs for the end-user (as a function of electricity and heat savings),

- Improved efficiency of fuel use (at least 25%),

- High level of fuel flexibility,

- Use of alternative fuels, including renewables and syngas, to reduce natural gas consumption

- Reduced emissions (up to 33%),

- Independence and security of power supply,

- Improving the energy performance of buildings,

- Supporting the electricity grid & helping the integration of intermittent renewables

## Emission Reduction

Depending on the technology used, the electrical efficiency of a micro-CHP unit ranges from 20% (for Rankine cycle and Stirling engine) up to about 60% (for solid oxide fuel cell). In terms of thermal efficiency, it can reach between 40% and 80% for different types of technologies. Therefore micro-CHP, in general, has the potential to reduce CO2 emissions and reduce primary energy consumption compared to a conventional boiler with electricity drawn from the grid. Depending on the scenario, micro-CHPs can save about 240-300 PJ of primary energy per year, or about 0.5-0.6% of the total energy used in the EU-27 in 2010 (where 1 PJ equates to approximately 31.6x106 m3 of natural gas). Based on that, greenhouse gasses can be reduced by 13-14 Mton of CO2-eq/year by using micro-CHP systems instead of gas boilers (equivalent to about 0.3% of the total EU-27 GHG emissions in 2010).

A recent study from Delta – ee [33] shows that buildings account for 36% of CO2 emissions in the EU. In this context, the MGT technology has been identified as one of the most suitable technologies to lower GHG emissions. The use of a clean fuel, such as natural gas, and the nature of the combustion allows MGTs to reach very low levels of polluting emissions.

Current MGT technology can reach a 59% reduction in carbon dioxide (CO2) and 95% reduction in nitrogen oxide (NOX) emissions compared to traditional systems. This is achievable thanks to the advanced combustion technology. Within MGT combustors, the chemical energy conversion of fuel into thermal power is much more controlled than other comparable technologies; the combustion chamber design is optimized to control formation of NOX such that emissions are up to an order of magnitude lower than in other combustion engines. The reduced temperatures of premixed flames inhibit the formation of nitrogen oxides while the excess of air instead restricts unburnt CO. Currently MGTs are inherently clean and do not require the use of abatement systems on the exhaust gas.

## Financial Cost/Benefit Analysis

A financial cost/benefit analysis for a MGT system depends on the type of application, and even within the same application, there are a number of variables to be taken into consideration.

As part of the OMSoP project, the University of Seville (USE) conducted a cost analysis comparing data retrieved from the literature to data coming from OEMs partners contributing to this summary. It should be noted that the analysis only considered manufacturing costs related to the MGT, and as such, costs related to the other components, equipment installation, and company profit were not taken into consideration. The analysis reveals that manufacturing costs are strictly related to the production rate with a range between 200€-600€. Fig. 4.3 shows the relation between specific MGT cost and production rate

Figure 4-3: Specific manufacturing cost comparison

Another variable which influences the MGT cost is the electric output. Though the relation between cost and electric output is not linear, the greater the electric output over time, the lower the cost. The graph below shows this relation based on the data supplied by Compower for MGT units between 5-60 kW.

Figure 4-4: Specific manufacturing cost of the micro gas turbine vs. net electric output for 1000 units/year production rate

Considering the additional costs associated to the other components of the systems, like the recuperator, power electronics, package, and company profit, the MGT market price can range from 800 € to 2200 €/kW. Adding heat recovery increases the price by 100 € to 300 €/kW.

When it comes to maintenance, MGTs show a higher reliability compared to the competing technologies. Currently, most OEMs are targeting maintenance intervals of 5000-8000 hours with a lifetime of over 30000 hours. In some cases, the lifetime of the system may be extended significantly with scheduled overhauls of specific components.

The economic viability of a MGT micro-CHP application is dependent upon the size of the unit being appropriate for the building and its loads, the payback period of the technology, and the Levelized Cost of Electricity (LCOE).  In such an application, it is necessary to consider the time profile of the energy consumption in terms of the heat/power ratio. The heat/power ratio is an important characteristic in energy consumption that is represented by its average amount as well as the degree to which the ratio deviates from the average during a reference time period (day, week, etc.). Indeed, the presence of strong ratio irregularities in energy consumption could lead to a higher energy cost, and thus, to a higher difficulty in identifying the sources of energy waste. A MGT CHP system is very flexible in terms of the ratio of heat to electricity production, allowing the system to better adapt to the needs of different users.

Business cases developed by the MGT OEMs shows that a MGT with micro-CHP may have a payback period of approximately 2-5 years at an average LCOE of 0.04-0.07 €/kWh.

The global energy efficiency of MGTs is high if compared with other technologies, due to the use of waste heat for cogeneration; moreover, their compactness and high power-to-weight ratio make MGT suitable for small installations in the real-estate and retail environment.

| Technology | Power Output | Cost |
| --- | --- | --- |
| Internal Combustion Engines | 4kW – 6MW | 600 – 4000 €/kW |
| Micro Gas Turbines | 3kW – 400kW | 900 – 2500 €/kW |
| Stirling Engine | 1kW – 3kW | 4000 – 8000 €/kW |
| Fuel Cells | 1kW – 20kW | 4500 – 30000 €/kW |

Table 4-1: micro-CHP technologies comparison

## Partnering with RES

Micro-CHP can play an important role in supporting renewables and meeting the challenges of the modern electricity grid. The technology is able to support renewables at the system level in Europe and can realise multiple benefits as a form of demand response, enabling householders and SMEs to change their electricity production and demand to suit grid conditions. There is also evidence that micro-CHP technologies can be connected together and controlled remotely as part of virtual power plants, supporting the grid and avoiding further grid and infrastructure investments [34].

The share of RES in the heating and cooling sector could also be expanded with the future development of various hybrid systems. The Optimised Microturbine Solar Power System project aimed to demonstrate the feasibility of using a MGT coupled with a CSP parabolic dish to provide energy for domestic and small commercial applications in the range of 5-30 kWe. The system may be used in a solar-only or hybrid (with natural gas or biogas) configuration in order to ensure the security of supply.

For a stand-alone, solar-only system, whose specifications are shown in table 4-2, the equipment costs would be in the range of 3014 to 3262 €/kWe (table 4-3) without accounting for transportation and installation.

Table 4-2: Summary of system specifications. Stand-alone, solar-only system with base-case technology (simple recuperative cycle)

Table 4-3: Summary of purchase equipment cost (PEC) for the stand-alone, solar-only system with base-case technology (simple recuperative cycle)

For a stand-alone, hybrid system, the equipment costs would be in the range of 3047 to 3302 €/kWe (table 4-4), without accounting for transportation and installation.

Table 4-4: Summary of purchase equipment cost (PEC) for the stand-alone, hybrid system with base-case technology (simple recuperative cycle)

A literature review done by the ETN WG has brought to the identification of costs for based and hybrid MGT technology.

Table 4-5: Cost comparison MGT-RES technologies

| TECHNOLOGY | POWER OUTPUT | PRICE |
| --- | --- | --- |
| NATURAL GAS | 3 kW – 400 kW | 900 – 2500 €/kW |
| OMSoP SOLAR | 5 kW – 50 kW | 3047 – 3302 €/kW |
| BIOGAS | 3 kW – 250 kW | 1000 – 2500 €/kW |

In the short term, such hybrid systems would allow a higher integration of RES into the grid by absorbing the fluctuations and by using natural gas, biogas, industry waste gas or landfill gas. In the long term, they would contribute to the achievements of the EU Climate and Energy targets set to decarbonise the energy system and to the full deployment of RES in the grid while ensuring security of energy supply.

# Policy Context

## EU Policy Framework

The priority of the European Commission is to develop its Energy Union Strategic Framework to ensure security of supply, affordability and sustainability of energy production. This strategy would facilitate the achievement of the goals of the 2050 low carbon economy Roadmap. The challenge of reducing greenhouse gas (GHG) emissions by at least 80% compared to 1990 levels in a secure and affordable way, would require an effective and balanced implementation of renewable energy sources (RES), increased energy efficiency improvements as well as carbon capture and storage.

Advancements in energy technology are vital if Europe's 2030 and 2050 targets are to be fulfilled. Combined Heat and Power (CHP) systems with RES (e.g., Concentrated Solar Power and Biomass) are technologies acknowledged by the European Commission in the Strategic Energy Technology (SET) Plan. Adapting the current energy scenario into a truly sustainable one will require realizing the full potential for renewable energy sources to satisfy the heating and cooling demand. There will be equal efforts necessary from both generation and end-use sectors in order to achieve these ambitious targets for 2030.

MGT have a large potential to become a highly important power generation source for different applications, especially when combined with heat recovery systems. In an EU context where the demand for heating power amounts to 46% of EU final energy use, and where 40% of that energy consumption is related to buildings, MGT CHP systems can easily justify their place in the future energy sector.

According to the studies of the International Energy Agency, in 2012, just 43% of the energy input was converted to electricity with thermal power plants, while co-generation power plants converted 61% of input energy into final electricity and heat. It is evident that one potential path towards a decarbonisation of the energy production involves increasing the share of electricity production using CHP, which currently accounts for 11% of the total power generation in Europe. Micro-CHP has gained interest in recent years due to its potential for providing efficient, clean and cost effective energy for homes and small businesses. The main advantages of such systems are the provision of electrical and thermal energy wherever it is required, eliminating transmission losses and reducing the cost of energy infrastructures. The share of CHP in the total energy mix can and should be much higher, which will contribute significantly towards meeting Europe’s climate and energy goals.

Biomass and Solar energy sources can further improve the decarbonisation of energy production by integrating them with CHP systems. This integration would lead to a reduction in electricity production costs for biomass and solar based systems through a technology specific mix of decreasing investment and maintenance costs, increasing electric efficiency and availability, and reducing electricity price for the end-consumer compared to electricity from the grid due to instantaneous use.

The MGT technology is a promising technology that is finding its position in the market thanks to its flexibility of RES integration and to the lower costs compared to other technologies, as highlighted in the benefits/costs analysis in chapter 4. The current technology allows distributed CHP to be adaptable to MGTs that can be integrated with RES (e.g., CSP and biofuels).  This would allow for CO2 neutral power generation and cut down the cost of transportation compared to centralised systems. However this poses challenges that are specific to the cycle configuration. Current technologies can only handle specific types of biofuels and are commercially viable in large scale, limiting their widespread deployment for distributed generation. The availability of suitable “CO2 neutral fuel”, as well as fuel flexibility (for improved reliability and availability) for small scale CHP, are among the major challenges that need to be addressed adequately to strengthen the interest for the technology. The availability of intelligent monitoring tools that can support non-expert end users is also an important challenge to address in order to enable the development for this technology.

## Policy Recommendations

The decarbonisation of the future European energy system should guarantee the same level of reliability as the existing one. This can be achieved by deploying technologies already commercialised or in the late development stage. According to the most recent studies, the energy consumption in 2050 will grow about 40% compared to today’s need. It is evident that the future demand can’t be fulfilled without a mix of sources, which at the same time will enhance supply security.

The RES capacity’s share will continue to grow and have a predominant position in the energy scenario, according to the priorities set by the European Commission in the SET-Plan. However, some of the main challenges towards the achievements of the EU 2050 targets are not sufficiently addressed. While focusing on the development of the future RES technologies and their implementation in the networks, there is the risk of ignoring the issues of system and market integration, which will become a critical priority in the coming years.

A high share of RES in the long term brings along extraordinary benefits, among which are reduced fuel costs and the reduction of greenhouse gas emissions. Nevertheless, in the short term, costs related to the operation of combined cycle power plants should be taken into consideration. It is necessary to balance the entire energy system and adapt long term energy policies that will encourage the deployment of RES, and at the same time, facilitate the ultimate decarbonisation of the energy system.

The backup technologies for low load factor dispatchable capacity are yet uncertain. Currently, the potential alternatives seem to be:

- Flexibilisation of Combine Cycle Power Plant

- New gas-fired plants

- Biomass/biogas fired plants

- Hydrogen-fueled plants

- Development of new energy storage technologies

All these options should be developed in parallel with the RES technologies, leaving few uncertainties in the market. Given the low levelised cost of electricity and the emissions regulations in place, utilities are not willing to invest further in existing or new assets for centralised power generation, which, according to the EU targets, should be dismantled in the near future. The utilities are therefore looking at Distributed Generation (DG), in which MGT can find its position. However, there are still some policy issues limiting the development of DG technologies. Besides the security of supply, the connection to the distribution grids and networks are the main issue. Determining how to incorporate the potential public benefits into the tariffs has been largely discussed in Europe. For example, to reduce the farm waste, site owners are given incentives to install power generating equipment that utilises biomass or biogas.

The next step to enhance the installation of DG technologies should be to allow users to generate their own power and transmit the excess to the neighbours. Currently, the transaction costs for both small power generation technology owners and large power plant owners are the same, limiting the competitiveness of small DG technologies.

# Requirements on Deployment

Though MGT is a secure and established technology on the market, there are some barriers to overcome in order to expand its position in the market. The ETN MGT Working Group has analysed and discussed the barriers for the deployment of MGTs, as well the advantages it may bring to the energy market.

## Investment and Market Barriers

According to the market analysis made by Navigant Research, the annual revenue from microturbine installation is expected to surpass $1 billion by 2020.

The use of MGTs in oil & gas, CHP, and CCHP applications represent strong growth opportunities for a technology which is still in a niche market. Furthermore, with the shift in Europe from centralised to decentralised power generation, an increased rate of MGT installations is forecasted, though the rates set by current energy utility providers, and the uncertainty in natural gas prices, will influence the development of MGT networks.

The table 6-1 summarises the main barriers and drivers for the deployment of MGTs in the current energy market.

|  | Barriers | Drivers |
| --- | --- | --- |
| Policy and regulations | - Economic efficiency - Lack of interconnection standards | - CHP and CCHP improving energy efficiency - Incentives to reduce emissions - Reduced fuel consumption in buildings |
| Market | - High gas prices - Low LCOE - Lack of connection between OEMs with distribution and marketing. | - Current electricity price volatility for industry sites. |
| Maintenance and installation | - Lack of customer expertise on the technology - Infrastructural issues related to the provision of the fuels needed | - Increased reliability and availability for energy sensitive applications |

Table 6-1: Deployment of MGT in the current energy market

## Recommendations & Important area of cooperation

To be able to run a MGT system for power and heat supply with competitive cost attributes, a number of investments in MGT system components must be made. This chapter discusses in details the investments needed for each component.

### Recuperator

| Biogas | - Increased effectiveness - Corrosion resistance - Clogging/fouling resistance - Lifetime |
| --- | --- |
| Biomass | - Increased effectiveness - Increased performance at lower temperature - Lower backpressure at higher mass flow - Lifetime |
| Solar | - Increased effectiveness - Lower backpressure at higher mass flow - Lifetime |
| Back-up RES | - Increased effectiveness - Cycles resistance lifetime |

Table 6-2: MGT recuperator research activities

Investments in:

- R&D on special materials

- R&D on special design for higher effectiveness

- Special manufacturing process for lower production cost

### Turbomachinery

| Biogas | - Increased TIT - Increased efficiency - Corrosion resistance - Wear resistance - Lifetime |
| --- | --- |
| Biomass | - Increased efficiency at lower speed - Increased performance at lower temperature - Wear resistance - Lifetime |
| Solar | - Increased efficiency - Increased performance at lower temperature - Wear resistance - Lifetime |
| Back-up RES | - Increased efficiency at part load |

Table 6-3: MGT turbomachinery research activities

Investments in:

- R&D on special materials

- R&D on coatings

- R&D on special aero design for compressor and turbine

- Special manufacturing process for lower production cost

### Combustion system

| Biogas | - Higher TIT - Corrosion resistance - Lower emissions - Wear resistance - Lifetime |
| --- | --- |
| Biomass | - Wear resistance - Lifetime |
| Solar | - Higher temperature resistance - Corrosion resistance - Wear resistance - Lifetime |
| Back-up RES | - Lower emissions - Cycles resistance - Lifetime |

Table 6-4: MGT combustion research activities

Investments in:

- R&D on special materials

- R&D on special design for lower emissions

- R&D on special coatings

### Power electronics

| Biogas | - Increased efficiency |
| --- | --- |
| Biomass | - Increased efficiency - Higher grid micro-interruption resistance |
| Solar | - Increased efficiency - Higher grid micro-interruption resistance |
| Back-up RES | - Increased efficiency - Power factor correction - Grid code compliance - Connection with energy storage - Off grid capability |

Table 6-5: MGT power electronics research activities

Investments in:

- R&D on special materials for IGBTs

- R&D on special design

- R&D on special software

- Special manufacturing process for lower production cost

# Bibliography

| [1] | J.-E. Hanssen, A. Riikonen, C. Noren, G. Karlsson, L. Malmrup, S. Ernebrandt, R. Stockholm, B. J. Veland, F. Fock, Mosbech, Hakon, J. de Wit and A. H. Pedersen, “Operating experiences from 18 microturbine applications for CHP and industrial purposes,” OMES, 2004. |
| --- | --- |
| [2] | T. Bayar, “Microturbines take on the market,” Cogeneration & on-site power production, pp. 21-24, October 2015. |
| [3] | NewEnCo, “Turbec T100 Microturbine,” [Online]. Available: http://www.newenco.co.uk/combined-heat-power/turbec-t100-microturbine. [Accessed 1 August 2016]. |
| [4] | AEBIOM, “Statistical Report - European Bioenergy Outlook,” AEBIOM, 2015. |
| [5] | J. Schmidt, B. Krautkremer and G. Grassi, “The Strategy of decentralised power stations: the potential of biomass in liberalised grids,” 12th European Conference and Technology Exhibition on Biomass for Energy, Industry and Climate Protection, Amsterdam, 2002. |
| [6] | D. Bohn, Micro Gas Turbine and Fuel Cell - A Hybrid Energy Conversion System with High Potential, Aachen, 2005. |
| [7] | D. N. Lymberopoulos, “Microturbines and their application in bio-energy,” European Commission - DG TREN, Pikermi Attiki, 2004. |
| [8] | S. S. M. O. W.P.J. Visser, “Development of a 3kW Microturbine for CHP Applications,” Journal of Engineering for Gas Turbines and Power, April 2011. |
| [9] | W. P. J. Visser, S. A. Shakariyants, M. T. L. d. Later, A. H. Ayed and K. Kusterer, “Performance Optimization of a 3kW Microturbine for CHP Applications,” ASME Turbo Expo, Copenhagen, Denmark, 2012. |
| [10] | D. Bars, A. Perrone, L. Ratto, D. Simoni and P. Zunino, “Radial inflow turbine design through Multidisciplinary optimization technique,” ASME Turbo Expo, Montreal, Canada, 2015. |
| [11] | L. R. G. R. F. S. P. Z. A. Perrone, “Multi-Disciplinary Optimization of a Centrifugal Compressor for Micro-Turbine Applications,” ASME Turbo Expo, Seoul, Korea, 2016. |
| [12] | A. J. Head and W. P. J. Visser, “Scaling 3-36 kW Microturbine,” ASME Turbo Expo, 2012. |
| [13] | O. Lammel, H. Schütz, G. Schmitz, R. Lückerath, M. Stöhr, B. Noll, M. Aigner, M. Hase and W. Krebs, “FLOX Combustion at High Power Density and High Flame Temperatures,” J. Eng. Gas TUrbines Power 132 (12), 121503-1 121503-10. |
| [14] | T. Zornek, T. Monz and M. Aigner, “Performance analysis of the micro gas turbine Turbec T100 with a new FLOX-combustion system for low calorific fuels,” Applied Energy 159, 2015. |
| [15] | A. Schwärzle, T. O. Monz and M. Aigner, “Thermal Incineration of VOCs in a Jet-Stabilized Micro Gas Turbine Combustor,” ASME Turbo Expo 2015: Power for Land, Sea and Air, Montreal, Canada, June 2015. |
| [16] | R. Lückerath, W. Meier and M. Aigner, “FLOX combustion at high pressure with different fuel compositions,” ASME Turbo Expo 2007: Power for Land, Sea and Air, Montreal, Canada, May 2007. |
| [17] | S. L. Hamilton and A. Chambers, “Microturbines, Distributed Generation: a non-technical guide,” PennWell Corporation, USA, 2001. |
| [18] | Capstone Turbine Corporation, “Capstone Low Emissions Microturbine Technology, White Paper,” Capstone Turbine Corporation, USA, 2000. |
| [19] | M. A. Rosa do Nascimento, L. de Oliveira Rodrigues, E. Cruz dos Santos, E. E. Batista Gomes, F. L. Goulart Dias, E. I. Gutiérrez Velásques and R. A. Miranda Carrillo, “Micro Gas Turbine Engine: A Review,” Federal University of Itajubá, Brazil, 2014. |
| [20] | B. L. Capehart, “Microturbines,” College of Engineering, University of Florida, Florida, 2014. |
| [21] | DBFZ GmbH, “Stromerzeugung aus Biomasse - Preliminary Report,” DBFZ Deutsches Biomasseforschungszentrum gemeinnützige GmbH, June 2013. |
| [22] | J. Zanger, T. Monz and M. Aigner, “Experimental investigation of the combustion characteristics of a double-staged FLOX-based Combustor on an atmospheric and a micro gas turbine test rig,” ASME Turbo Expo: Power for Land, Sea and Air, Montreal, Canada, June 2015. |
| [23] | W. Mattews, “Additional engine testing of an advanced alloy for microturbine primary surface recuperators,” ASME Turbo Expo, 2006. |
| [24] | O. O. Omatete, P. J. Maziasz, B. A. Pint and D. P. Stinton, “Assessment of recuperator materials for Microturbines,” Oak Ridge National Laboratory, Oak Ridge, 2000. |
| [25] | D. Aquaro and M. Pieve, “High temperature heat exchangers for power plants: Performance of advanced metallic recuperators,” Applied Thermal Engineering, Volume 27, 2007. |
| [26] | E. Bianchi and G. Boschetti, “Cogenerazione e trigenerazione con microturbine a gas,” Ansaldo Energia. |
| [27] | Sandvik Data Sheet, “Engineering Properties of Alloy 713”. |
| [28] | SECO, “The essential material characteristics of MAR-M-247,” [Online]. Available: http://www.secotools.com/it/Global/Segment-Solutions/Aerospace-Solutions/AS-Material-main/Heat-resistant-super-alloys/Inconel-71873/. [Accessed 27 July 2016]. |
| [29] | J. Wahl and K. Harris, “An overview of advanced Ni-based superalloys for small turbines and missile engine applications,” ASME Turbo Expo, 2010. |
| [30] | D. Vicario, “High Efficiency Microturbine with Integral Heat Recovery,” DoE EERE Research Reports, 2005-2015. |
| [31] | A. Sommers, Q. Wang, X. Han, C. T'Joen, Y. Parkd and A. Jacobi, “Ceramics and ceramic matrix composites for heat exchangers in advanced thermal systems - A review,” Applied Thermal Engineering, Volume 30, 2010. |
| [32] | H.-T. Lin and M. K. Ferber, “Characterization of Mechanical Reliability of Silicon Nitride Microturbine Rotors,” Key Engineering Materials Vol. 287, 2005. |
| [33] | Delta-ee. [Online]. Available: http://www.cogeneurope.eu/medialibrary/2015/05/19/d6648069/miro-CHP%20study_merged.pdf . |
| [34] | LichtBlick, “Virtual Power Plant Concept which integrates RES, micro-CHP, electric vehicles and the smart grid”. |
| [35] | European Parliament, “DIRECTIVE 2012/27/EU OF THE EUROPEAN PARLIAMENT AND OF THE COUNCIL,” 25 October 2012. [Online]. Available: http://eur-lex.europa.eu/legal-content/EN/TXT/PDF/?uri=CELEX:32012L0027&from=EN. |
| [36] | C. R. Stucley, S. M. Schuck, R. E. H. Sims, P. L. Larsen, N. D. Turvey and B. E. Marino, “Biomass Energy Production in Australia,” RIRDC, 2004. |
| [37] | LichtBlick, Virtual Power Plant Concept which integrates RES, micro-CHP, electric vehicles and the smart grid:. |

Average data given by the OEMs drafting this summary.

Source: EC- An EU Strategy on Heating and Cooling, 16 February 2016

Compared to importing electricity from the grid and using boilers to generate heat

According to models ran by Delta-ee, micro-CHPs technologies can reduce CO2 emissions by 17%-33% in a typical German family home compared to covering energy needs by an advanced condensing boiler and electricity from the grid. Retrieved from: http://bit.ly/1PmrmMc

Ecuity. The role of micro-CHP in a smart energy world. Retrieved from http://www.ecuity.com/wp-content/uploads/2013/03/The-role-of-micro-CHP-in-a-smart-energy-world.pdf

Data compared with the “Catalog of CHP Technology – Section 5. Technology Characterization – Microturbines, U.S. Enrvironmental Protection Agency Combined Heat and Power Partnership”.

ARTICLE Micro turbine boom predicted by 2020 – Navigant research