## Sheet1
ISO TC 142 - WG9 - Part 4 Offshore & Marine
Offshore environment - what is in the air | What is Part 4 test procedure trying to achieve | What is Part 4 test procedure trying measure
Air intake filtration systems for Gas Turbines employed in offshore applications must contend with an ever changing environment with varying airborne contamination, namely: | In the absence of any current recognised harmonised global test standard, this proposed test methodology is to as fas and scientifically as possible replicate offshore real world conditions, with varying airborne contamination that an offshore air intake filtration system will typically have to contend with. Furthermore the behaviour of an air initake filtration system changes as the filtration component is subject to changing atmospheric conditions and loadinig with contamination.
Furthermore, the performance of the air intake filtration system has a direct correlation to on Gas Turbine performance, namely: Fion efficiency against platform generated pollution. Dp rise. Dp stability. Number of cycles (water challenge and/or RH). Water leakage. Filtration efficiency against naturally occuring sea salts.
Platform generated pollution - diesel/gasturbine engine outlets, hydrocarbons, drilling dusts, mud burn and grit blast to name a few. Harmattan/Shamal - land-produced dust like contamination suspended in the air out at sea. | Filtration products that are tested iin accordance with part 4, shall also be tested in accordance with part 1 - simulating filtration performance against platform generated pollution/Harmattan/Shamal i.e. dusts. | Filtration efficiency against airborne particulate (part 1) - platform generated pollution/ Harmattan/Shamal.
Fogs and mists (saline water droplets) - periodic on many occasions frequent and prolonged. Sea spray and sea salt aerosols (saline water droplets) - generated during periods of high seas and wind speeds. | Primary water deluge challenge (clean "test object") - simulating filtration performance against fogs, mists, sea spray, & sea salt aerosols (clean condition). Water deluge challenge (heavy fog at 40m visibility) - simulating filtration performance against fogs, mists, sea spray & sea salt aerosols (loaded condition). | Dp rise, Dp stability, number of cycles and water leakage - fogs, mists, sea spray & sea salt aerosols (clean condition). Note: for filters that do not pass this stage will not be considered as suitable for offshore applications, test to cease in this instance. Dp rise, Dp stability, number of cycles and water leakage - fogs, mists, sea spray & sea salt aerosols (dirty condition).
Sea salts - constant loading with sea salts, hygroscopic behaviour, constantly fluctuating with RH, thus in a transitional phase from dry to wet and wet to dry. <40% RH in dry phase, >70% RH in wet phase. Ability to increase/decrease in size when phasing. | Salt loading (continuous) - simulating filtration performance against sea salts. | Filtration efficiency against airborne particulate salt - sea salts.
Fluctuating relative humidity - a cyclical ever changing condition, which is influenced by periods of rain, fogs and mists, leading to extremely high humidity. | Relative humidity cycles - simulating filtration performance against fluctuating relative humidity. | Dp rise, Dp stability and number of cycles - fluctuating relative humidity and the effects of RH on arrested salt (hygroscopic).
Additional ISO comments
ISO comment | ETN response
The test is too complicated, I don’t know what it is trying to achieve. | Please see table above.
RH ramping up and down – does it have to be linear?’ Answer NO, providing the approach is standard in all rigs and specified. Also, that the behaviour of salt changes with RH, thus the ramp rate is important to have a consistent condition in the rigs, so that the behaviour of the salt and its effect on the filter cannot be different in rigs. | The loading with a sea salt aerosol (SSA) during the test procedure is to replicate the constant SSA loading an offshore air intake filtration systems is subject to. The SSAs are hygroscopic in behaviour, constantly fluctuating with RH and are in a transitional phase from dry to wet and wet to dry ( <40% RH in dry phase, >70% RH in wet phase), with increasing/decreasing size and ‘dry/wet state’ when phasing. Thus, the condition of the SSA (dry, wet or transitional), concentration in the media and ‘dry/wet state’ will be directly affected by the RH, and thus SSA loading and RH will have an effect on the media porosity, media loading and media structure. Therefore, from a repeatability and a scientific approach perspective it is desirable to control the ramp up/down rates in the test procedure, to ensure that the behaviour of the arrested SSA is controlled relative to RH and thus control the effects on filtration performance that could be experienced in different test rigs if not controlled.
How repeatable is the SSA generator? | The SSA output was presented by AAF
Distribute actual test data to ISO committee – results/report from the testing done this far to support the method proposed | Documents available on the ETN website
Create a draft document that contains not only the salt testing which provided already but also incorporate the framework of the other parts – even not yet fully set or developed. This one of the comments (you need a defined draft document) | ETN will commence to work on this when classification, failures and other requirements have been addressed in the WG