## Sheet1
Index | Status | UGM 2017 Category | UGM 2018 Category | UGM 2019 Category | UGM 2020 Category | UGM 2021 Category | UGM 2022 Category | Model | Engine Model | Package | System | Component name | Failure Mode | RCA Performed | Cause | Effect | Mitigation measures | Observations | Company | Provided by | Siemens - Slide No | Siemens - Response by | TCT - Slide No | RWG - Slide No | Comments
23.3 | Open |  | CAT-1 | CAT-1 | CAT-1 | CAT-1 |  | 24GT61, 24GT62, DLE | 24GT DLE | Turbomach | Compressor | Bearings | HP Thrust Bearing Failure | Yes | Environmental conditions but not believed to be conclusive |  |  | - Event occurred in 2015 - Cracked bearing cage - Damaged ball bearings | E.ON | Martyn Boden | 2018.A.16-18 | S Broomfield | 2018.27-33 |  | [Users Steering Committee] (2019) Ask Siemens to give updates on announced material review [User Group](2021) Update requested on the status of HP Thrust Bearings failures and experience since material review was implemented
105 | Open |  |  | CAT-2 | CAT-2 | tbd | CAT-2 | 24GT61 | Dual Fuel Conventional Combustor | Turbogenerator | Power Turbine | Power Turbine Rotor | Power turbine alignment difficult to achieve due to the unbalance of the power turbine casing on its supports | No | Center of gravity location | Loss of time. Additional downtime. |  | Loss of references for alignment work. Time consuming activity | Total | Dominique Orhon
106 | Open |  |  | CAT-2 | CAT-2 | tbd | CAT-2 | 24GT61 | Dual Fuel Conventional Combustor | Turbogenerator from Mount Vernont | Power Turbine | Nozzles Module D | Positioning Key is able to enter in other holes after rotating slightly module D | No | No mechanical coding. No failsafe alignment | Additional downtime. Loss of time. |  | Wrong assembly, loss of time. Position Key on D module not effective. D module has to be removed for locking PT and when putting it back, it can be installed rotated because the key on the module and lifting tool are not good enough and can be “bypassed” | Total | Dominique Orhon
107 | Open |  |  | CAT-1 | CAT-1 | tbd | CAT-2 | 24GT61 | Dual Fuel Conventional Combustor | Turbogenerator | Power Turbine | Inboard Bearing Seals | Different designs developed during manufacturing phase | No | Mixing design arrangements. | Oil migration to the power turbine disk. Fire HiPo in the exhaust |  | Initial design was with knife edge seal + closed smiley face and scavenged drain. Final design was no knife edge seal + open smiley face + open drain. | Total | Dominique Orhon |  |  | 2019.55-61 |  | [User - Author](20190409) Design is not secured during engineering study. [TCT](20190426) Is this a design issue/redesign currently being worked on by Siemens? [User-Author](20190502) Yes. From Mount Vernon.
108 | Open |  |  | CAT-1 | CAT-2 | tbd |  | 24GT61 | Dual Fuel Conventional Combustor | Turbogenerator | Oil System | HP Oil Pump | Pump Distress | No | Unknown | No HP Oil Available |  | Issue is not necessarily followed properly because the oil system is equipped with a back-up oil pump | Total | Dominique Orhon |  |  | 2019.62-65 |  | [TCT](20190426) Is this a Cascon Pump type? More clarfication required on the scenario that resulted in lack of oil, issue with back-up pump also?
109 | Open |  |  | CAT-1 | CAT-1 | tbd | CAT-2 | 24G56 | Single Fuel Conventional | Turbocompressor | Combustor | Plates Behind Fuel Injectors | Distress after 8000 hrs when running with H2S | No | Hot Corrosion | Leads to engine removal. Necessitate the replacement of the combustor after 8 000 hrs |  |  | Total | Dominique Orhon |  |  | 2019.68-69 | 2019.31 | [TCT](20190426) Please confirm which part is in question. Is this part of the Plates & Carriers assembly which forms a type of "piston ring" over the Fuel Injector to seal with the Outer Combustion Casing (04 Module Casing)? Why was the Combustor deemed to require replacement? [User - Author](20190502) This is the square plate surrounding the nozzle passage. [User Group Meeting](2019) Is there currently an active R&D project from Siemens (or a Service Provider) to mitigate/reduce significantly the effects of hot corrosion on SGT-A35?
110.2 | Open |  |  | CAT-1 | CAT-1 | tbd | CAT-1 | 24G56, 24G62, 24GT61, 24GT62, DLE | All | Turbogenerator, Turbocompressor | Power Turbine | Power Turbine | Only Siemens to overhaul the power turbine. No ISP's | No | No licenses from Siemens. Lack of competition and alternatives | Additional OPEX and delay. |  |  | Total | Dominique Orhon |  |  |  | 2019.25 | [User - Author](09042019) No competition is not acceptable. [User Group Meeting](2019) Users shared their concerns regarding the lack of alternatives for RT Power Turbines overhaul (mainly RT61), and asked Siemens to address the issue.
111 | Open |  |  | CAT-1 | CAT-1 | tbd |  | 24GT61 | Dual Fuel Conventional Combustor | Turbogenerator | Water Mist | Electrical Cables | Burning cables during water mist release because steam is too hot in some location for the cables, especially for the cables feeding enclosure light blocks. | No | Water mist release with hot components of the engine | Replacement of cables and light blocks. Higher OPEX and higher downtime. |  |  | Total | Dominique Orhon |  |  | 2019.66-67 |  | [TCT](20190426) Can the cause be clarified? What is the source of the water/steam leakage in to the package and has this been corrected? Has the water mist hit the hot engine external casings and turned to steam which then evaporates onto the cables causing burning or corrosion? [User - Author](20190502) Water and steam come from the fire fighting deluge system. TCT is right the water mist hit the engine and turn to steam and burns cables (no particular corrosion).
112 | Open |  |  | CAT-2 | CAT-2 | tbd | CAT-2 | 24GT61 | Dual Fuel Conventional Combustor | Turbogenerator | Low Speed Shaft Lines | Low Speed Shaft Lines | Defective Lateral Analysis | Yes | Quill shaft not considered as a rigid coupling | Package delivery is delayed. Higher CAPEX for manufacturer due to additional rework. |  | Generator running on a critical speed around 1500 rpm | Total | Dominique Orhon |  |  |  |  | [TCT](20190426) More details required - quill shaft for what component in the package? [User- Author](20190502) Quill shaft is part of the low speed shaft of gear box. Gear box connection is a rigid flange to flange connection to the generator.
114 | Open |  |  | CAT-3 | CAT-3 | tbd | CAT-2 | 24GT61 | Dual Fuel Conventional Combustor | Turbogenerator | Power Turbine | Instrumentation | Very difficult access to the power turbine instrument due to barrel arrangement of the power turbine. | No | Access very limited. | Loss of time during instrumentation replacement. Additional downtime impacting availability. |  |  | Total | Dominique Orhon
115 | Open |  |  | CAT-1 | CAT-1 | CAT-1 | CAT-1 | 24G56, 24G62, 24GT61, 24GT62 | All | Turbogenerator and Turbocompressor | Power Turbine | Power Turbine Disks and Rotor | Life Assessment | No |  | Generate unnecessary inspections and overhauls. Higher OPEX and higher downtime |  | Life management of PT: Main components lifed for 150kh. Inspection at 100kh, and component assessment criteria exist only to give 50kh. It should be possible to develop inspection techniques and criteria to go for another 100kh cycle. Additionally, if main rotor components are overhauled early (E.g.: 50kh), there are no inspection criteria allowing these components to do their initial potential. | Total | Dominique Orhon |  |  |  |  | [User Group Meeting](2019) Users highlighted incoherences in the maintenance strategy and requested Siemens to provide further input regarding the inspection of the Power Turbine disk and rotor, and the status of development of inspection criteria to allow these components to run for another 100khrs after inspection at 100khrs, or earlier. [User Group](2021) Update requested on PT life extension/assessment of remaining life User Group 2022 Siemens to provide update on disk life assessment of PT to limit unnecessary scrap rate (creep and cyclic life) + PT disk inspection criteria
116 | Open |  |  | CAT-1 | CAT-1 | tbd | CAT-2 | 24G56, 24G62, 24GT61, 24GT62 | Duel fuel and Signle Fuel Conventional Combustor | Turbogenerator and Turbocompressor | Axial Compressor | Abradable Components | Abradables of HP compressor come out in chunks | No | Unknown | Potential DOD in the engine during running conditions |  |  | Total | Dominique Orhon |  |  | 2019.70-75 | 2019.18-19 | [TCT](20190426) Can operator verify if abradable originates from the HPC Rotor path or the HPC Labyrinth (Knife) Seal Paths? Was this discovered during operation via borescope or during overhaul? [User Group Meeting](2019) Users highlighted that this issue increases the risk of DOD in the engine during running conditions.
117 | Open |  |  | CAT-2 | CAT-2 | tbd | CAT-2 | 24G56, 24G62, 24GT61, 24GT62 | Dual Fuel and Single Fuel Conventional Combustor | Turbogenerator and Turbocompressor | Starting System | Clutch | Starter crash re-engagement | No | Not defined | Starting sequence aborted. Downtime impacting availability. |  |  | Total | Dominique Orhon |  |  | 2019.86-89
101.2 | Open |  |  | CAT-1 | CAT-1 | tbd | CAT-1 | DLE | 24C DLE |  | Combustion | DLE System | Fail to meet LCP BREF emission limit | [5 empty] | Centrica | Steven Fuller |  |  | 2019.24-27 | 2019.20-23 | [User - Author](20190116) Our LTSA manager has not yet found after 6 months who in their organisation is responsible for framing their consultation with the EA or compliance with new legislation. We have a 24C DLE with long combustors that they are only willing to test to a FAT NOx pass off of 42mg/Nm3 (we actually achieved somewhat better at 20). Historically (last 5 years) however site stack monitoring behind an RT62 has given values of 55-90 mg/Nm3 depending on load ambient and accumulated hours, typically NOx is almost 2 x FAT and CO almost ½ FAT values with no explanation from Siemens as to the reasons. [TCT](20190426) Can mapping improve the emissions performance? How often do you optimise for emissions? [User - Author](20190501) We do not optimise emissions on site due to our site measured emissions being somewhat different to those on the test bed for reasons unknown (impact of downstream PT?) and it is not always possible to arrange production loads to test across the range. When we FAT’d our current engine we discovered that Siemens / RWG do not optimise on the test bed either (cost of gas?) and we had to insist on test bed optimisation. What we discovered somewhat coarsely was that NOx emissions could be optimised through primary zone temperatures achieving 4-5 vppm spreads in the midrange and 2vppm at our upper powers. Operating the engine to its capability (above our site 100% performance point) resulting in the NOx tending toward a common value as expected. Siemens / RWG appear to place most emphasis on the build tolerances in order to improve emissions. Our current position is that the test bed is the place to optimise emissions because of the more controlled environment. [User Group Meeting](2019) Siemens to comment on the status of their group project on engine emissions, and if NOx emissions improvements are envisioned as a result of this project.
110.1 | Open | CAT-2 |  | CAT-1 | CAT-1 | tbd |  | 24G56, 24G62, 24GT61, 24GT62, DLE | All | Turbogenerator, Turbocompressor | Power Turbine | Power Turbine | Concerns regarding the options for RT61 Power Turbine overhauls |  |  |  |  | Houston is the only option and this facility does not have the best track record in terms of QA (second assembly issue in 2018 due to a misaligned PT unit) Also for European customers the Duty and Delivery charges are very high when compared with shipping to say RWG in Aberdeen | E.ON |  |  |  |  | 2019.25 | [User - Author](07032019) Could we survey any other ETN RT61 operators for their views and feedback prior to the conference
118 | Open |  |  | CAT-2 | CAT-2 | tbd | CAT-2 | 24G56 | Single Fuel Conventional Combustor | Turbocompressor | Exhaust | Exhaust Cone | Corrosion of the welding located on exhaust cone after 2 years of operation | No | Welding quality | Heat radiation and potential exhaust fumes release in the enclosure |  | Happen after 2 years of operation. Issues is potentially related to welding quality and characteristics of the welding material. | Total | Dominique Orhon
119 | Open |  |  | CAT-1 | CAT-2 | tbd |  | 24G56, 24G62, 24GT61, 24GT62, DLE |  |  | Exhaust |  | High Temperature Spread at exhaust | no |  | Alarm warnings and trips, due to the temperature at position 14 largely deviating from the temperature profile average |  | High exhaust temperature spread on a 24G DLE engine used in a compressor station when operating at high load. No issues found related to thermocouples or clamping points, but fine metal chips were found in the gas path before the secondary fuel nozzle. Origin of these chips has not been identified | Open Grid Europe | Samuel Strack |  |  | 2019.45-47 |  | [TCT](20190426) More specific details required (spread profile, magnitude of spread against limits, were alarms tripped, were ESDs tripped, GT-DLE and G-DLE? Not SAC?) What troubleshooting was performed to understand cause of the spread? [User Group Meeting](2019) Observations field was updated. Users and Service Providers recommended taking into account the swirl pattern which should affect the location of the temperature spread as the load changes. CTS documents should be available from Siemens
120 | Open |  |  | CAT-1 | CAT-2 | tbd |  |  |  |  | Oil System | Pump | Oil leak |  | Defective seal on pump shaft |  | Oil collected and hose installed to redirect leaked oil |  | Open Grid Europe |  |  |  | 2019.62-65 |  | [User - Author](09042018) PAB is available: PAB-02-0008-01 CASCON Lube Pump Mechanical Seal Leakage (Mar 2019) Interest in experience from User who have faced a similar leakage and/or applied the PAB
121 | Open |  |  | CAT-1 | CAT-1 | tbd | CAT-2 | 24G56, 24G62, 24GT61, 24GT62, DLE |  |  |  |  | Possible Hexavalent Chromium findings |  |  |  |  | Yellowish residue found Several OEMs have circulated Service Bulletins on the health risk of Hexavalent Chromium, the actual situation for RB211 engines is unclear | Open Grid Europe |  |  |  | 2019.10-16 | 2019.26 | [User Group Meeting](2019) Presence of Hexavalent Chromium, Cr (VI), was confirmed on SGT-A35. Independent Service Providers shared their best practices to reduce safety risk.
122 | Open |  |  | CAT-1 | CAT-1 | CAT-1 | CAT-2 | 24G56, 24G62, 24GT61, 24GT62, DLE |  |  | Other |  | Spare parts lead time excessively long |  | Spare parts usually reach the User after 8 or 9 months | Higher OPEX and higher downtime |  | Delay applies even for licensed service providers (TCT, RWG) | Open Grid Europe |  |  |  | 2019.38-39 | 2019.24 | [User Group Meeting](2019) The User community underlined their urgent need for more reasonable lead time for spare parts. They invited Siemens to react and improve this point. (user group 2022) Please provide an update.
123 | Open |  |  | CAT-1 | CAT-1 | CAT-1 | CAT-1 | DLE |  | Turbomach | HP-Turbine | HP-Turbine blades | Sudden failure of a blade occurred 11,280 hours after the 50,000 h overhaul and caused serious damage to the HP / IP and PT's downstream blade and vanes. | In process, feedback from SIEMENS to the RCA from failed blade is pending. | unknown | both engine GG+PT removal and general overhauled | renovation all HP/IP blades/vanes and all renovation or repair all | Failed from full load | Stadtwerke Muenster | Rainer Böschen |  |  | 2019.48-54 | 2019.28-30 | [User Group Meeting](2019) The User Community requested input and explanations from Siemens regarding the recent HPT blade failure event (2018), and risk for the fleet. [User Group](2021) Update requested on findings and actions taken for the fleet
124 | Open |  |  |  | CAT-1 | tbd |  |  | SGT-A35 24G |  | Gas Compression | ZA-2011 | Tripping on Center Bearing LO dp - Suspect High Flow on start up | Basic 5 Whys | TBC | High dp | Adjustment of K Factor on flowmeter on start up |  | Shell Global Solutions | Matthew Hull |  |  |  |  | Provided by David Park
125 | Open |  |  |  | CAT-1 | tbd |  |  | SGT-A35 24G |  | Gas Compression | ZA-2011 | Center Bearing failure - 2018 | Yes - Full investigation | Oil Quality/Overhaul management/Engine handling | Unit tripping out on speed probe failures | Engine replacement - Improved Oil management and overhaul management strategy |  | Shell Global Solutions | Matthew Hull |  |  |  |  | Provided by David Park
126 | Open |  |  |  | CAT-2 | tbd |  |  | SGT-A35 24G | Multiple | Lube Oil |  | LO pump failure – Argotech pumps | No |  | Only a single pump available |  | Multiple units (3 in the UK at the same time) have all experienced failures of LO pumps, leading to a single pump being available. | Shell Global Solutions | Matthew Hull
128 | Open |  |  |  | CAT-1 | tbd |  | DLE |  |  | Control | Control system | Procedure to commission a DLE engine after overhaul: FT-110/125 controls & STI187 (question details in comment) | [5 empty] | Shell Global Solutions | Marcel van Zijp |  |  |  |  | [User - Author](20200720) Follow-up question to #104 (2019 meeting) The procedure for DLE commissioning is detailed in Siemens Technical Instructions STI187, which includes procedure for mapping and subsequently configuring the ECS with updated parameters (applicable to both FT110 & 125) Ask Siemens to share and explain associated technical instruction STI187.
129 | Open |  |  |  |  | tbd |  |  | SGT-A35 24G RT56 |  | Control System (FT-125) | Overspeed Testing | Preferred method(s) of overspeed testing | N/A | Difficult in performing overspeed tests and checking for un-revealed failures. Our prefered solution is testing the overspeed loop in parts: tripping the unit to test final elements and using frequency generators offline to test logic solvers. Use of frequency generators was not mossible without ECS modifications due to protections in place to trip the engine when there is a speed demand discrepancy. There is a jumper that can be added in the control cabinet to allow operator to run engine to trip speed, but this does not find unrevealed failures and is not preffered in terms of running up to trip speed. | Unable to properly test the overspeed system without ECS modifications. | Control system modifications made to introduce an "overspeed test mode" that can be enabled when offline | What is the proposed method for overspeed testing in the design of the control system? (that meets the requirements of proof tests and associated standards) | Shell Global Solutions | Matthew Hull
130 | Open |  |  |  |  | CAT-1 | CAT-2 | 24GT62 | RB211 24GT | Compressor package | Combustion | Other | Number of Failed starts not reaching light off and idle | on-going | Not identified | Unplanned stop | None | Swap of engine after the IPC failure reduced the failed starts, but it is still present with 2 to 3 failed starts at start-up | Equinor | Runar Blom Sørlid
136 | Open |  |  |  |  | CAT-1 | CAT-2 | 24G56, 24G62, 24GT61, 24GT62, DLE | All |  | Lube Oil System | Lube Oil System | -Question- Clarification required on lube oil specification change – modification for sampling d/s of filters | [5 empty] | British Petroleum | Niall Ewart
137 | Open |  |  |  |  | CAT-1 | CAT-2 |  |  |  | PT | RT62X | -Question- Any experience of the RT62X upgrade yet?
138 | Open |  |  |  |  | CAT-1 | CAT-2 | [5 empty] | -Question to Siemens Energy - Please detail Siemens support performance,with clear explanation of the support organization post the major re-org within Siemens – how are the different services (design authority, engineering, overhaul, OE build etc) distributed within the organization. How can this be used to improve performance going forward?
139 | Open |  |  |  |  | CAT-1 | CAT-1 | 24G56 | RB211-24G | Gen Set | PT RT56 | RTD's cross wiring terminals inside bearing housing | instrument failures | yes | Excitations from the PT rotor | Trip due to lack of temperature signals | None |  | Equinor | Runar Blom Sørlid |  |  |  |  | Recommend Siemens to make the RTD with longer lengths so it is possible to use the outside mounted junction box •W53A-41.1 Equinor would like SE to evaluate if journal bearing pads (front and rear) and thrust bearings pads with RTD with 6m cable to connect to external junction box.
141 | Open |  |  |  |  | CAT-1 | CAT-1 | 24G56, 24G62, 24GT61, 24GT62, DLE |  |  |  |  | General Point - Update on Supply chain shifr RR->SE | [5 empty] | Total | Pablo Bellocq |  |  |  |  | NEW Point during call: Users invite Siemens to provide an update on the supply chan shift from RR to SE. (highlighting parts not yet fully available in new supply chain, stock of critical parts, typical lead times for critical parts and impact on overhaul programs).
142 | Open |  |  |  |  | CAT-1 | CAT-1 | 24G56, 24G62, 24GT61, 24GT62, DLE |  |  |  |  | Update on burning alternative fuels in A-35 (H2, NH3, Bio fuels...) | [5 empty] | Total | Pablo Bellocq |  |  |  |  | New topic during call: Update on burning alternative fuels in A-35 (H2, NH3, Bio fuels...)
143 | Open |  |  |  |  | CAT-1 | CAT-1 | [5 empty] | Update on fuel valve controllers | [5 empty] | Total | Pablo Bellocq |  |  |  |  | New topic during call: Please provide update of the new Meggit controllers: number of running units with latest design, proven wire length capability, reliability figures if available, delivery time for new controllers and for spare controllers)
144 | Open |  |  |  |  | CAT-2 | CAT-2 | [5 empty] | TCT test bed cross calibration/Category | [5 empty] | Total | Pablo Bellocq |  |  |  |  | New topic during call: Please provide an update on the planning for the upgrade of test bed of TCT and cross calibration program.
23.1 | Open |  | CAT-1 | CAT-1 | CAT-1 | CAT-1 |  | 24G62 | RB211-24G-RT62 |  | Compressor | Bearings | The HP Thrust Bearing revealed extensive spalling affecting the ball bearings and Outer Raceway. It was also noted that the Bearing Cage had fractured at one ball pocket location. | Yes |  | chip detector | replaced bearing | failure at 16.113 hours. BRG replaced at RWG worshop in Aberdeen (Jun/2008) | Petrobras |  | 2018.A.16-18 | S Broomfield | 2018.27-33 |  | [TCT] (2018) There is insufficient detail to allow TCT to formulate a specifi response. Can operator provide investigation report or additional details for TCT review? [Users Steering Committee] (2019) Ask Siemens to give updates on announced material review. [User Group](2021) Update requested on the status of HP Thrust Bearings failures and experience since material review was implemented
23.2 | Open | CAT-1 | CAT-1 | CAT-1 | CAT-1 | CAT-1 |  | 24G62 | 24G62 | RR | Compressor | Bearings | Thrust Center Bearing Module 3 QDM High Particles Number | No | none | Loss of production. Leads to remove the engine in advance. Leads to change the bearings every 25000 hours preventively. | User is exchanging bearing every 25000 hours. |  | Total |  | 2018.A.16-18, 2017.18-21 | S Broomfield | 2018.27-33 |  | [Users Steering Committee] (2018) mitigation measures are not acceptable [TCT] (2018) insufficient information to provide a full answer. Can discuss general bearing RCA principes. [Users Steering Committee] (2019) Ask Siemens to give updates on announced material review [User Group](2021) Update requested on the status of HP Thrust Bearings failures and experience since material review was implemented
66 | Open |  | CAT-1 | CAT-1 | CAT-1 | CAT-1 | CAT-2 |  |  | Turbogenerator, Turbocompressor | Fuel | Fuel metering valve | Leaks from fuel metering valves |  |  |  | RCA output required |  | British Petroleum |  | 2018.A.24-31 | R Gibbins | 2018.34-35, 2019.17-23 |  | [Users Steering Committee] (2018) User, please provide more details / Siemens, please provide feedback on the WG with fuel valve (presentation) [TCT] (2018) Can customer provide additional information? How old are the valves? What is the maintenance history of the valves? What troubleshooting has been performed? [Siemens] (2018) Please refer to presentation. We have seen a significant improvement in Gas FMV reliability over the last couple of years following a number of improvements made to the valve and control system. However, leakage across the internal stem seals has emerged as a significant issue for some operators. This issue whilst notable across the wider fleet, appears to be isolated to only some operators. The main cause gas leakage is believed to be contamination of the stem seal. Valves retuned for RCFA have been found to have fibber contamination around the seal. There are several improvements under development, most notable an improvement to the seal to include a wiper, reducing the impact of contamination within the fuel. [Users Steering Committee] (2019) Keep monitoring. New product available end 2018, any feedback already? [TCT](20190426) Can it be confirmed which type/model of FMV is being used? [User Group Meeting] (2019) With a new design introduced in 2019, the User Community would be interested in the feedback from Users and Service Providers. [User-Author](2021) Request update on experience and performance with new 2019 FMV design
71 | Open | CAT-2 | CAT-1 | CAT-1 | CAT-1 | tbd |  |  | RB211 | Various | Instrumentation | Other | Level of unit trips is over double that of equivalent units of similar size in similar applications. | No | Various causes on different instrumentations and systems sometimes just a temp speratic spike. | On going restarts | Often just try restarting | Siemens is already investigating a trip reduction program based on actual impact to unit vs. potential problems that could be handled better as an alarm. Users group in Asia has agreed to provide feedback for this initiative. | Exxon Mobil |  | 2018.B.23-33 | R Gibbins | 2019.81 |  | [TCT] (2017) Understand more the nature of the trips and develop an underatinding of the most problematic sensors. Ensure you calibrate your instruments on an annual basis. [Siemens] (2017) Siemens recognises that there is opportunity to improve and rationalise the Alarm and Trip philosophy for the Industrial RB211 and will be undertaking a programme of work this year to reduce the number of trips and improve how signal faults are managed to maximise up time of the machines. Further information on this programme of work will be available towards the end of the year and in the mean time Siemens will be engage with customers to obtain there input. [Users Steering Committee] (2018) Request to Siemens: please provide a presentation on trip - package and core engine [Siemens] (2018) Please refer to presentation. Siemens has completed phase one of a programme of work to rationalise the alarms and Trips. This first phase covers 7 subsystems and removes or improves the logic for ESD, CS and alarms. These systems are now available as an upgrade [Users Steering Committee] (2019) We keep monitoring Siemens' alarms and trips rationalisation programme. [User Group Meeting](2019) Siemens to comment on the status of their alarms and trips rationalisation programme initiated in 2017
82 | Open |  | CAT-1 |  |  | CAT-1 | CAT-2 | 24G56 | RB211-24G | Gen Set | Other | Other | Oil leakages internal, front IPC | No | Unknown | Unplanned stop | Engine exchange | Lube oil outside on IP Casing, leakages from IPC front and oil coking inside balance piston. No findings at engine overhaul that could explain the oil leakage. | Equinor |  | 2018.A.34-36 | S Broomfield | 2018.36-39 |  | [Users Steering Committee] (2019) Follow-up from User needed [User - Author](20190415) Updated Still on-going the swap of engine did not solve the issue, medium power operation 10 to 15 MW at Oseberg A Main power unit C We are investigating on back pressure on the vent line from tank and as well the separator element being integrated part of the tank (Pos 5), this has never been replaced or cleaned.
27 | Open |  | CAT-3 | CAT-3 | CAT-3 | tbd |  | 24G62 | 24G62 | RR | Compressor | Vanes | Rubbing of the OGV 7th stage inner damping medium creating DOD into HP compressor which damage all blades and vanes located downstream | No | None for the time being | Loss of production. Leads to remove the engine in advance. | Overhaul of the engine | Rivet maintaining the upper and lower inner dumping medium were found damaged. | Total |  |  | S.Broomfield |  | 2019.32-36 | [Siemens] (2018) Recommend vane feet are fully repaired at every overhaul. Inspection requirements for shroud rings have been increased. PAB 02-0006. New design of IPOGV available in 2019. [User Steering Committee](2019) Is the new solution available?
43 | Closed | [7 empty] | RB211 24C | Power Gen | Enclosure / Auxiliaries | Other | Failure to start | Yes | concervative timers and excessively low purge speed | poor start reliabiltiy | timer increased to industry standard an purge speed to be increased |  | Shell Global Solutions
32 | Closed | [6 empty] | 24G62 | RB211 - 24G - DF | Power Gen | Control | Other | Unit shutdown and loss of control to unit |  | Overload of communication card | Unit shutdown and loss of control to unit | Communication card replaced. Comms errors rectified |  | Shell Global Solutions
72 | Closed | [6 empty] | DLE | RB211 - DLE | Compressor | Instrumentation | Transmitters | RVDT failure on VIGV | No | Transit damage | Failure to start | Replace component |  | Shell Global Solutions
73 | Closed | [6 empty] | 24G62 | RB211 - 24G - DF | Power Gen | Instrumentation | Transmitters | Vibration probe reading incorrectly | No | Proximitor failure | High vibration readings and alarm | Replaced proximitor |  | Shell Global Solutions
97 | Closed | [7 empty] | 24 G |  |  |  | Clutch mechanism | [5 empty] | GAIL (India) Limited | [5 empty] | [Users Steering Committee] (2018) More details needed
102 | Closed |  |  | CAT-1 |  |  |  | 24GT62 | RB211 | Compressor package | Lube Oil | IP/HP bearing | Flooded engine due to closed valve on drain line from oil separator(Dollinger) unit with oil accumulation in dollinger unit and overfilled oil tank on shutdown and flooded engine via the L5 vent line. | RCA completed | Isolation valve closed (Valve installed by User and not standard in the package design) | Flooded engine with need to swap engine and drain HP drum | Isolation valve have been included on the PID and locked open |  | Equinor | Runar Blom Sørlid
103 | Closed |  |  | CAT-1 | CAT-1 | CAT-1 |  | 24GT62 | RB211 24GT | Compressor package | IP Turbine rotor | IP Turbine blade | IP Turbine blade disintegrated in operation after 49k hours since new | Completed | Trailing edge crack (slow propagating initiated early in life of the blade). | Engine removal both GG and PT (PT server damages to blades and vanes) | inspect and overhaul blades at regular 25k interval and boroscope IP turbine blades per manual |  | Equinor | Runar Blom Sørlid |  |  | 2019.40-44 | 2019.28-30 | [TCT](20190426) - Was a Failure Analysis performed? - What was the root cause? - Confirm this is an RB211-24GT SAC? - Any T455 (EGT) spread issues? - Any other operating anomalies? [User-Author](20190506) - RCA carried out - No reason found, refers to “abnormal” cyclic loading as a possible cause, but cannot find any of this from our operational data - This is 1880-4030 (SAC) - No we do not have any spread issues, but we are operating at @ 790 rating (T455avarage=777 C) - None [User Group Meeting](2019) Siemens is required to communicate regarding IP turbine blade failures across the fleet, and if a root cause has been identified. [User Group Meeting](2020) Siemens is required to communicate regarding IP turbine blade failures across the fleet, and if a root cause has been identified. There have been several similar incidents. [User-Author](2021) Findings from latest IPC stg 6 shroud failure showed flow disturbance/separation at max power. Can this also have been a contributor to the IP Turbine blade failure ? Confirmed by Siemens: Aerodynamic excitation of the IP compressor stage 6 vane will have no effect on the IP turbine blade
104 | Closed |  |  | CAT-1 |  |  |  | DLE |  |  |  |  | Procedure to commission a DLE engine after overhaul | [5 empty] | Shell Global Solutions | Marcel van Zijp |  |  | 2019.28-37 |  | [User - Author](20190405) 1. Which control settings (like low extinction point, noise islands etc.)needs to be adapted/changed when an overhauled or spare engine is installed on site? 2. Where to obtain this data; from the performance test report, data logs or engine logbook? 3. How to configure this in the FT-110/125 controls? 4. What are the consequences if these settings are not correct? 5. Is it required to check and adjust those values in between overhaul?
113 | Closed |  |  | CAT-3 |  |  |  | 24GT61 | Dual Fuel Conventional Combustor | Turbogenerator | Bearings | Bearings | Oil migration to the Bleed of Valve | Yes | Pitch and Roll over +/- 6.5° | Oil migrates to the compressor and to the bleed of valve. Black carbon deposit on the bleed of valve |  |  | Total | Dominique Orhon |  |  |  |  | [User - Author](09042019) Does another operator experience the same issue?
127 | Closed |  |  |  | CAT-1 | CAT-1 |  | 24GT62 | SGT-A35 RT62 | Compressor Package | IP compressor and High pressure compressor HPC | IPC stg 6 shroud disintegration and following HPC Blade stg 1 | high cycle fatigue crack | Completed, focus on the IPC shroud stg 6 | IPC stg 6 Shroud failure | Engine removal | Monitoring unit, until new stg 6 shroud design is available | TBD | Equinor | Runar Blom Sørlid |  |  |  |  | [User - Author](20200902) Engine failed in operation severe damage to HPC this due to IPC stg 6 shroud failure New IPC stg 5 and 6 vanes introduced is being evaluated to use the Gzero design. These have redesigned aerofoils to remove the aerodynamic excitation and therefore do not require filling with rubber for vibration damping.
131 | Closed |  |  |  |  | CAT-1 |  | 24G56 | RB211-24G | Compressor package | PT RT56 | Rim cooling | Measurement fault | No | TBD | Unplanned stop | Proper installation ensure thermocouples have the correct insertion de | Not installed properly | Equinor | Runar Blom Sørlid |  |  |  |  | after several trials we finally managed to install the probes correctly, ensure thermocouples have the correct insertion depth.
132 | Closed |  |  |  |  | CAT-1 |  | 24G56 | RB211-24G | Compressor package | HP Compressor | 1-2 stg disc HP compressor rotor | Crack, interstage weld crack | No | Unknown | Replaced part at overhaul |  |  | Equinor | Runar Blom Sørlid
133 | Closed | [7 empty] | test | test | test
134 | Closed | [7 empty] | test | test
135 | Closed |  |  |  |  | CAT-1 |  | 24G56, 24G62, 24GT61, 24GT62, DLE |  |  | PT |  | -Question- PT depot capability & capacity: where is the capability, what are (actual) turnaround times and (actual) capacity. Today, and future plans | [5 empty] | British Petroleum | Niall Ewart
11 | Closed |  | CAT-1 |  |  |  |  | 24G62 | RB211-24G-RT62 |  | Compressor | Bearings | Front bearing case rivet broken | No |  | Chip detector | Replaced bearing | Failure at 9.168 hours BRG replaced at SIEMENS worshop in Macaé-Brazil (mar/2008) | Petrobras |  | 2018.A.21-22 | S Broomfield | 2018.27-33 |  | [Siemens] (2018) Please provide further information to allow Siemens to form a comprehensive response. E.g. ESN, when event occurred, engine hours, any RCA information, Siemens RCI or salesforce reference. [TCT] (2018) There is insufficient detail to allow TCT to formulate a specifi response. Can operator provide investigation report or additional details for TCT review?
24 | Closed | CAT-1 | CAT-1 | CAT-2 |  |  |  | 24G62 | 24G62 | RR | Compressor | Blades | Stage 5 & 6 HPC Cycle Fatigue | No | HCF happens at low ambient temperature. | Leads to engine removal. | none | During the user meeting in Milan, vanes of stage 5 and 6 was treated but the issue was on the blades of stage 5 and 6. | Total |  | 2018.B.3-5, 2017.44-46 | S Broomfield | 2017.18-24, 2018.49-50, 2019.82-84 |  | [User - Author](20190409) No other high cycle fatigue on stage 5 and 6 blades since 2016. [TCT](20190426) On the last repair/Overhaul, were any checks done in order to verify there were no signs of HCF on the stg. 5 and 6 blades? [User - Author](20190502) Yes, trace of HCF were observed.
3.2 | Closed |  | CAT-1 | [5 empty] | RB211 - DLE | Compressor | Combustion | DLE System | combustor failure | No | High combustion noise | reduction in engine life | replace engine |  | Shell Global Solutions |  | 2018.A.9-13 | R. Gibbins | 2018.21-26 |  | [TCT] (2018) Can operator provide additional information? What exactly has failed? How many combustors failed? What troubleshooting was conducted and what were the findings? [Siemens] (2018) Please refer to presentation. Generally we do not see many issues with the DLE DCN cracking in service. Some wear on the side cheeks of the DCN is normal at 25K hours and to avoid in-service failures the exit casting of the DCN is replaced at overhaul. The DCNs and combustor hardware is expected to achieve mid-life O/H as long as noise levels are managed to within defined limits (different limits for long & Short DLE variants). Running with high noise will lead to increased ware of the DCN location dog, side checks and further increase noise. If not addressed, high noise and increased ware of the side cheeks will likely lead to cracks of the DCN side cheeks. [Users Steering Committee] (2019) Keep monitoring the topic [User] (2019) Item was raised to explore potential risks of failure, item 3.2 can be closed
3.1 | Closed |  | CAT-1 | CAT-1 |  |  |  | 24G62, DLE | RB211 24G DLE | Cooper Rolls | Combustion | DLE System | Unable to run engine. High hazard to destruction of the combustor and turbine | In process | High combustor noise | Discharge Nozzle Cracks | Replaced by new one from stock | Cracks at the POT8 DN were first time detected 13 000 operating hours after overhaul (engine 1790-808). The cracked DN was replaced by overhauled one. Then during the annual inspection after 1800 operating hours the same DN was found in poor technical condition (Worn Condition). We are afraid of damaging the DN and then also the turbine blades | Eustream |  | 2018.A.9-13 | R. Gibbins | 2018.21-26 |  | [TCT] (2018) Can operator provide additional information? What exactly has failed? How many combustors failed? What troubleshooting was conducted and what were the findings? [Siemens] (2018) Please refer to presentation. Generally we do not see many issues with the DLE DCN cracking in service. Some wear on the side cheeks of the DCN is normal at 25K hours and to avoid in-service failures the exit casting of the DCN is replaced at overhaul. The DCNs and combustor hardware is expected to achieve mid-life O/H as long as noise levels are managed to within defined limits (different limits for long & Short DLE variants). Running with high noise will lead to increased ware of the DCN location dog, side checks and further increase noise. If not addressed, high noise and increased ware of the side cheeks will likely lead to cracks of the DCN side cheeks. [Users Steering Committee] (2019) Keep monitoring the topic
28 | Closed |  | CAT-1 | [7 empty] | Compressor | Inlet Guide Vane (IGV) | IGV out of position causing trips |  |  | Unit trip - Currently have a procedure at every water wash to lubricate the VIGV mechanical moving parts, take oil samples for Hydraulic oil maintenance, and a calibration of the VIGV's? TS-0075 | FCO 1683, Rev 01 Has been submitted for approval, Agil and Mehti will provide an update |  | British Petroleum |  | 2018.B.8-13 | R Gibbins | 2018.44-46, 2019.77-80 |  | [Users Steering Committee] (2018) package and operator related - follow OEM instructions [User] (2018) there are still concerns with this system. In case where new 2 Ram system was fitted, we haven’t seen any big improvement. Please provide updates from last year (item #18)" [Siemens] (2018) Please refer to presentation. A number of improvements were developed following an investigation conducted in 2015/16 focused on maintenance activity, troubleshooting documentation and some software improvements. Reported VIGV events in ORAP have since reduced and the issue of VIGVs has moved significantly down the Fleet disruption index. We are aware of some isolated issues and the need to create better visibility of the software improvements. Siemens will be issuing a PIB in the coming months to improve customer awareness of the improvements available.
62 | Closed | CAT-2 | CAT-1 | CAT-3 |  |  |  | 24G56, 24G62 | RB211-24G | All | Fuel | Other | Liquid Fuel manifold | No | Dual fuel engines: coking of manifolds on dual fuel engines due to lack of purging of the liquid running on gas | Spread and start-up problems | Overhaul of manifold |  | Equinor |  | 2018.B.16-20 | S Broomfield | 2017.94, 2018.52 |  | [Siemens] (2017) Low levels of coking inside diesel manifolds is typically present at overhaul. However quantities sufficient to cause starting, spread and transfer problems in operation are unusual. Where these have occurred poor diesel quality has been identified. Low utilisation has also been identified as a factor as the fuel can degrade in the static areas of the system. In this case regular starts and/or transfers on diesel have been recommended to flush out degraded diesel. [TCT] (2017) Overhaul of Manifold regularly. Ensure you have spares of the LFM and burners. Change the liquid fuel filter annually. Carry out fuel changeovers and run at high loads on liquid fuel. [Users Steering Committee] (2018) updates required [Siemens] (2018) See presentation [TCT] (2018) No changes [Users Steering Committee] (2019) The new routine was implemented in 2017, we keep monitoring
79 | Closed |  | CAT-1 |  |  |  |  | 24G62 | RB211-24G-RT62 |  | Other | Other | Pawl Carrier broken | Unknown |  | Start-up problem | Pawl Carrier overhaul | failure at 21.300 hours. Pawl Carrier overhauled at at RWG worshop in Aberdeen (Mai/2017) | Petrobras |  | 2018.A.39-41 | S Broomfield | 2018.40-43 |  | [TCT] (2018) Can operator provide more information related to this failure? Is this a spring failure or pawl failure? Has the engine sustained starter crash engagements?
90 | Closed | CAT-1 | CAT-1 |  |  |  |  | 24G56, 24G62 | RB211-24G | Cooper Package - Mechanical driver (gas production E&P) | Power Turbine | Other | Power Turbine RT 62 has repeat infant mortality failures of instrumentation following PT overhaul (internal vibration probes, internal bearing temperature probes). | In process | poor / incorrect installation during manufacture / overhaul of PT. | Machine trips on instrument failures | Over ride the signal, true mitigation requires PT to be removed and overhauled again as the instrumentation is internal and not accessible externally. | User had experience of such failures on this PT (RT62) on various units and multiple companies. | Centrica | Package Solutions Engineering | 2017.137-139 | D. Brown |  |  | [Siemens] (2017) Not aware of a particular problem with PT shaft instrumentation generally, so suggestion is that most problems are installation issues (FSR competance)? RTDs with thicker leadwires (24 AWG) introduced ca. 1996, originally for simplex, then duplex RTD's. Difficulty can be encountered with routing wires out of bearing housings, sometimes requires modification to accommodate. Sharp corners should also be addressed on installation to avoid earth faults. Care to be taken not to trap leads when installing bearings / covers, also clip leads properly to prevent windage damage. Incorrect reading can be caused by RTD head not being correctly installed into bearing pad. Terminal strip inside casing can be cause of poor connections, deleted mid-1990's along with introduction of Hermetic Seals. Vibration probes; No known particular issues with reliability? Correct procedure for setting probe gap detailed in O&M Manuals / GEM 0054. [Users Steering Committee] any updates? [Siemens] (2018) A presentation on this subject was provided at ETN 2017 but no feedback was received from delegates. More information is required if further response is to be provided. See also Item 71.
76 | Closed |  | CAT-1 | [5 empty] | RB211-24G-RT62 |  | Maintenance | Power Turbine Overhaul | First overhaul at 100khrs. Lack of clarity over the inspection regime required after first overhaul. Original advice was first inspection at 150khrs but conflicting information received that inspection interval may be at 125khrs |  |  | Inspection requires significant diassembly with associated down time. | User has many RT62 units approaching 100K. Need clarity on the options to overhaul PT. Siemens current advice is that standard overhaul scope will require regular in service inspection post overhaul. Need clarity on options. |  | British Petroleum |  | 2018.A.44-48 | D. Brown |  |  | [TCT] (2018) Currently Siemens is the only authorized option for PT Overhaul. (User Feb 2022) Update requested on the stationaries and blade casings. Do they have a life limit of 168khrs or can be used beyond if there is no face roll and creep.
93 | Closed |  | CAT-1 |  |  |  |  | DLE | RB211 - DLE | Compressor | Gas generator | Seals | Oil leak on seals | No | under investigation | reduction in engine life | replace engine |  | Shell Global Solutions |  |  |  | 2018.36-39 |  | [Siemens] (2018) Please provide further information to allow Siemens to form a comprehensive response. E.g. ESN, when event occurred, engine hours, any RCA information, Siemens RCI or salesforce reference. [TCT] (2018) Operator needs to provide more details. [Users Steering Committee] (2019) Closed. More details needed from the user to receive an answer
16 | Closed | CAT-2 | CAT-2 |  |  |  |  | 24GT62 | RB211-24GT RT62 | Compressor Drive | Compressor | Casing | Bleed Valve failing | No | Open | Unplanned stop | replace with new parts |  | Equinor, Total |  |  | S Broomfield | 2017.86, 2018.53-56 |  | [Siemens] (2017) We do see BOV failures but on base load operators the frequency is low. EHM will pick up leaking BOV's. Recommend BOV's are overhauled at shop visit. IPBOV failures more frequent on low power operations with BOV's open. Ref SB to inspect every 2K. [TCT] (2017) Which bleed Valve is failing? IP or HP Handling? Check that they are not running open. Controlled only by the Dunlop Solenoid Valve. Energised Closed which closes Handling bleeds. Is prone to getting stuck, so when ECS sends closing signal it may not move. Even thouugh ECS indicates it is closed. (no physical feedback/limit swittch) . Remove Dunlop Solenoid Valve at 8k hour intervals and check for freedom of movement. [Users Steering Committee] Please expand OEM response, any update? [Siemens] (2018) For the later standard of IPBOV dish which does not have slots, a solution to add shims is available. This removes the sress concentrations caused by the bolts. Recent evaluation of compressor perfornance has shown that BOV opne/close point cane be reduced. This removes the root cause of the duct cracking which is exitation by air exiting the BOV's. Changes to the BOV schedule require a controls change which is available on request.
5 | Closed |  | CAT-2 |  |  |  |  | DLE | RB211 - DLE | Compressor | Combustion | DLE System | Fail to start / no flame | No | torch supply pressure | fail to start | increase supply pressure |  | Shell Global Solutions |  |  | R.Gibbins |  |  | [Siemens] There are several issues which have been seen in service with DLE failure to start. A few examples are: 1) Blockage of the torch injector(s) - contamination of fuel gas, or may occur following water wash. - Increasing the torch pressure may temporarily show an improvement. 2) Ignitions systems problems - ignitors, leads of the ignition unit itself - The RIC can be checked for faults. 3) Gas leaks from torch or central lines - Check pigtails - Drain valves. 5) Incorrect setting of the torch pressure - typically 5.5Bar but may need to be higher for some machines. " [User - Author](20190405) Supply pressure was increased to mitigate the problem.
6 | Closed |  | CAT-2 | CAT-2 | CAT-2 |  |  | 24G56 | RB211-24G | Gen Set | Combustion | Fuel Supply | Dual Fuel Burners erosion/cracking | No | 8000hrs | Unplanned stop | replaced burners | Erosion/cracking of burner tip after less than 8000hrs of operation since overhaul | Equinor |  |  | S.Broomfield |  | 2019.27 | [Siemens] Erosion and cracking of DF burners requiring replacement at 8K hours is very unusual. Typically DF burners only need cleaning and flow checking at 25K and can be refitted. We would need more details of the damage seen however fuel quality is most likely cause. [User - Author](20190412) We still experience this on the Oseberg C Gen Set B, from last inspection @ 19500hrs : Several burners found with missing material on the liquid fuel nozzle which appears to have been caused by carbon coking then thermal erosion of the material. [TCT](20190426) Is this a new topic for 2019? [User](20190506) It is an ongoing issue at Oseberg C only, SAC dual fuel engine.
56 | Closed |  | CAT-2 |  |  |  |  | 24G62 | RB211 - 24G - DF | Power Gen | Fuel | Fuel Supply | Unit failed to start on diesel | Yes | Valve sticking due to rust. Incorrect material on LFMV pressure regulator (carbon steel, should be stainless) | Failed to start | Service the pressure regulator. Laterly correct material supplied by the valve manufacturer. |  | Shell Global Solutions |  |  | R.Gibbins |  |  | [Siemens] The dp regulator within the Liquid fuel metering valve is sensitive to contamination and is known to stick if contaminated leading to failed starts. Typically the source of contamination is the fuel. we are not aware of any components within the valve which are know to rust but we are interested to understand more about this specific issue. [User - Author](20190405) Resolved; root cause known, item status closed.
53 | Closed |  | CAT-2 |  |  |  |  | DLE | RB211 - DLE | Compressor | Fuel | Fuel Valve | position failure of FMV | No | high wear rate of valve | fail to start | Replace FMV |  | Shell Global Solutions |  | 2018.A.24-31 | R Gibbins |  |  | [Siemens] Please refer to presentation. A number of improvements have been developed and we are confident that the issues of premature failure due to ware or the actually thrust bearing or ball screw has been resolved. Please also refer to PIB-01-0001. [User - Author](20190405) FMV was replaced, item status closed.
68 | Closed |  | CAT-1 | [7 empty] | Fuel | Liquid Fuel | Engine will not start or operate on Liquid Fuel. Deposits are present in every component including the DP Cell, FMV, in line filter, manifold, weight distribution blocks, extension tubes, and nozzles. |  |  | High spread on EGT, failure to achieve load, slow ramp during start-up. Severe coking of the Weight Distribution Balance piston. HSSE impact of changing manifold in the field needs to be assessed/monitored. | Eliminate extended periods of (stagnant) diesel in the fuel system while operation on Gas fuel. Requires regular operation on liquid fuel - Siemens to help define minimum frequency. |  | British Petroleum |  | 2018.B.16-20 | S Broomfield |  |  | [Siemens] See item #62 and presentation
69 | Closed |  | CAT-1 | [7 empty] | Fuel | Liquid Fuel | Many problems with liquid fuel (see item 68), Angola engines suffered blocking of on skid filters. Technical query around adequacy of 10micron filtration should we move to 5micron. |  |  |  | Siemens to provide guidance on benefits of 5micron filtration for on package filters. |  | British Petroleum |  | 2018.B.16-20 | S Broomfield |  |  | [Siemens] (2018) See #62 and presentation
88 | Closed |  | CAT-2 | [5 empty] | RB211 24C | Power Gen | System | Lube Oil System | Engine Flooded with oil | Yes | Contaminated / Dirty Oil | Blocked oil line, Machine tripped on high vibrations | Engine change Ensure oil is clean | See comments | Shell Global Solutions |  |  | D.Brown |  |  | [Users Steering Committee] need more information - observations from user ? To know how that occurs [Siemens] Oil flooding of GG can be caused by a number of factors; e.g. vent system issues, overfilling of LO reservoir (ref SB 133), drain-down of LO cooler on shutdown, oil migration from hydraulic starter system etc. in addition to scheduling valve issues. More information required to advise further. [User - Author](04042019) Unit was repaired and root cause investigation carried out. Results can be shared at next user group meeting. The main cause of engine oil flooding is the lube oil scheduling valve sticking in the incorrect position during the start sequence or maintenance runs. The high center bearing DP trip should protect against this during the start sequence although it is possible this may not be active during a maintenance run. The recommended practice is to disconnect the L1 supply line and the 3 scavenge lines and connect them to a piccolo tube for maintenance runs of the lube oil system to ensure no chance of feeding oil into the engine. The failure seems to be unique to this unit and is believed to be due to insufficient scavenge oil flow from the center bearing. The center bearing scavenge line has a tap off which scavenges oil from the starter gearbox which is normally supplied with oil from the H1 hydraulic supply line. On the flooded engine the hydraulic oil supply line to the gearbox was found to be blocked which meant no oil was being supplied to the gearbox and therefore the scavenge line was just scavenging air. As air is significantly less dense than oil the center bearing scavenge was preferentially pulling air from the starter gearbox and not enough oil from the center bearing which led to the center bearing overflowing after a while of scheduled oil flow. Other than ensuring the oil is clean to prevent a blockage of the gearbox oil supply nozzle we are yet to find a solution to prevent a future re-occurrence of the issue. The key lesson I have taken away is if there is a chance an engine has been filled with oil for example following a drop in synthetic oil tank level etc then it is essential further investigation is carried out before the engine is run again as this could result in failed turbine blades. For us a borescope of the engine quickly confirmed it had been oil flooded.
81 | Closed |  | CAT-2 |  |  |  |  | 24G62 | RB211 - 24G - DF | Power Gen | Other | Lube Oil System | Unit shutdown when rolling down - PCV opened | No | Failed pump delivery pressure PCV | Shutdown and loss of oil pressure to GBX and PT bearings | New PCV ordered |  | Shell Global Solutions |  |  | D.Brown |  |  | [Siemens] Is this connected to Item 80 ? Better definition of question required. Please provide further information to allow Siemens to form a comprehensive response. E.g. ESN, when event occurred, engine hours, any RCA information, Siemens RCI or salesforce reference. [User - Author](20190405) PCV replaced, item closed.
83 | Closed |  | CAT-2 | [7 empty] | Gas generator | Other | Compressor stub shaft corrosion. Angola experiencing high cost of refurbishment at GG overhaul. |  |  | High unplanned maintenance costs, reduced reliability |  |  | British Petroleum |  | 2017.48-60 | S.Broomfield |  | 2019.16-17 | [Siemens] See corrosion presentation from 2017. Note that corrosion on front bearing track does not present any reliability issues over a normal overhaul life. There have been no track or front bearing failures as a result of corrosion.
51 | Closed |  | CAT-2 |  |  |  |  | DLE | RB211 - DLE | Compressor | Fuel | Other | High spread | No | DLE manifold drain logic issue | trip on fuel mode changeover | Change logic |  | Shell Global Solutions |  |  | R.Gibbins |  |  | [Siemens] Build up of condensation within the Secondary fuel lane is often the main contributor to failed DLE transfers following long runs in central diffusion. Siemens can offer an upgrade to drain the Secondary lane while in Central Diffusion if this is a regular issues. Ref PIB-02-0001. In addition it is recommended that all drains are held open during a water wash sequence. On some units this was not configured but can be modified on request. [User - Author](20190405) Drain is added to secondary fuel line. Item closed.
52 | Closed |  | CAT-2 |  |  |  |  | DLE | RB211 - DLE | Compressor | Fuel | Other | Ignition failure | No | comm cables in ignition module heat damaged by failed anti-ice flexible | fail to start | Replace cables / repair anti-ice pipe |  | Shell Global Solutions |  |  | R.Gibbins |  |  | [Siemens] (2018) We are not aware of a common fleet issue with regards to failure of the ignition units or cables. Failed pipework's imparting hot air onto the ignition box and cables does present a risk of failure and should be rectified as soon as identified to avoid secondary damage to other equipment. [Shell 20190405] Unit repaired, item closed.
78 | Closed | CAT-3 | CAT-2 |  |  |  |  | 24GT61, DLE | RB-21124GT61 | Siemens (Rolls Royce) | Other | Other | operational Desk | No | language problem with spanish operators | more time to solve incidents | first line techncians in spain |  | Europac | M.Hill |  |  |  |  | [Siemens] (2018) The OSD continues to only operate in English with support from the regional teams as well as the wider community in the Warwick office. The OSD have contact details for a 24/7 team in Spain supporting non-AGT products that can act as an out of hours translation service if needed. [Users Steering Committee] Update required, has it been implemented ? [Siemens] (2017) Siemens have an extensive network of regional staff in regional offices who have the prime responsibility for supporting customers. In several cases, including Spain, this includes in country offices with Siemens employees speaking the local language. It is only when this first line of support is not available or otherwise unable to provide support to the customer first hand should the operational service desk (OSD) be contacted. Currently the OSD only supports customers in English and this is clearly stated when the OSD is advertised. However, this issue has been brought to the management of the Service Desk to consider providing a translation / interpretation service when needed."
70 | Closed |  | CAT-2 | [7 empty] | Gas generator | Other | Pt Aluminide coating on IP turbine blade has been replaced by sermalloy 1515. No technical justification provided by Siemens |  |  | Unknown coating reliability. Cost impact. | Siemens to provide technical background and experience with this coating. |  | British Petroleum |  |  | S.Broomfield |  |  | [Siemens] (2018) S1515 was original preferred coating for GT IPT blades as it is cheaper and has better sulphidation resistance. However a low fatigue test result during development resulted in early blades using Pl Al whilst the results were re-evaluated. Further analysis eventually concluded the the fatigue life would meet the design requirements so S1515 was standardised as mod1552 in 2005. POE for mod1552 was ESN4012 and ESN2026 so the majority of the fleet was built with this coating. At 25K the IPT blades are normally in good condition and can be left assembled in the disc. At 50K the blades are fully overhauled and the original Pl Al coating is removed and replaced with S1515. Thus most of the fleet now has S1515 coated blades with many engines achieving 50K without any IPT coating problems.
95 | Closed | CAT-1 | CAT-2 | CAT-3 |  |  |  | 24G56, 24G62 | RB211-24G | All | Turbine | Rotor | Curvic Coupling corrosion | No | Salt carry over | Corrosion/erosion | replaced with new parts |  | Equinor |  | 2017.48-60 | S.Broomfield |  |  | [Siemens] (2017) Ref item 19 [TCT] (2017) Corrosion issues & High scrap rate. Review TLRF and history [Users Steering Committee] fixing the filter should solve the issue [Siemens] (2018) See corrosion presentation from 2017. [User - Author](20190412) We have started a air filtration exchange program hopefully this will help out.
22 | Closed | CAT-2 | CAT-2 | CAT-3 |  |  |  | 24G56, 24G62 | RB211-24G | All | Compressor | Rotor | HP/IP Bearing Support (Spider) wear | No | HP/IP bearing support typically cracks in tubes and there are difficulties in realigning of the spider after repair. | Scrap of parts | Upgrade to latest version |  | Equinor |  |  | B.Glassey | 2017.57-61 |  | [Siemens] (2017) The Single skin HP/IP Bearing Support (Spider) is undergoing a suite of minor design-for-reliability and design-for-manufacturability changes based on the feedback from our customers and overhaul bases. These components improvements were launched within the AGT Gas Turbine team in Montreal in 2015. The first component is currently undergoing launch with the supplier and will be subjected to detailed first article inspection (FAIR). It is due to be delivery Q3 2018. The improvements will address oil service pipe fretting and leakage with the heatshields, IP7 Air tubes are being modified to eliminate possible reversed installation, resolving excessive stress and cracking on the tubes and finally the interface between the Casing and Struts is being improved to eliminate potential loosening of the fasteners. The improved bearing support, once successfully production rate proved will be used as standard in all new production Rb211. It is fully interchangeable with existing single-skin bearing supports in the fleet and will be made available for fleet operators for upgrade at approved overhaul bases. [TCT] (2017) Upgrade kit??, Doncasters repair issues, TCT moving fwd with hybrid solution (Doncasters repair pipes/brackets, TCT restore bry bore by M/C using engines own 05 casing). [Users Steering Committee] want update when it goes in service [Siemens] (2018) First hardware is expected December 2018 with first use in production engines from February 2019. As stated last year, it is completely interchangeable with existing standard. [User - Author](20190412) We are monitoring the effectiveness of all QA changes done at Doncasters after QA audit
92 | Closed | CAT-1 | CAT-2 | CAT-1 |  |  |  | 24G56 | RB211-24G-RT56 | All | Power Turbine | Seals | Damaged seals (stationary (3,4, 5) and rotating seals aft of the PT56) | In process | Seal out of roundness, lack of needed clearance & oil leaking between rotating seal and PT rotor shaft | Oil leakages, high vibration after trip, high oil consumption permamnent | change of seals | Power Turbine | MVM GTER, Equinor |  | 2017.141-143 | D. Brown |  |  | [Siemens] (2017) Presumably refers to PT Shaft Seal for RT56, however this is not a honeycomb seal - please also define ""stationary (3,4,5)""? Seal strip design, can sometimes be damaged / flattened on installation. Can often be straightened but requires rotor removal to accomplish. Important to carry out seal air test (GEM 0083) after installation to prove seal performance. Unusual for static part of seal to be damaged; if so requires removal of diffuser support which requires major disassembly. Outer part of seal (Exhaust adaptor) can be changed at rotor changeout & could be held as spare? Important to ensure seal air system set properly, if not embodied also consider provision of 'shop' air support at low powers / improved instrumentation per TB 0173. Is oil leakage internal or external? - if latter this may not be a function of poor seal performance. More info required regarding "high vibration following trip" - a temporary elevation in levels might be expected but this should return to normal levels once rotor fully heat soaked. [Siemens] (2018) A presentation on this subject was provided at ETN 2017 but no feedback was received from delegates. More information is required if further response is to be provided. [User - Author](20190412) PT RT56 with excessive oil consumption still occurs, swapping PT rotor and Exhaust adapter RT56-2-1E solves the issues. It is time consuming task to swap rotors as it takes 2 to 3 weeks. Problem seams to be more of a RT56 issue than RT62 can we do any changes to the design ? It does not appear that the oil leaks over the rotating seal and it is more likely that it find it's way under the rotating seal. We know that Siemens applies RTV as sealant but questions if it helps ? [TCT](20190426) The root of this issue appears to have been determined. Is this fix something that has been required more than once? I.e. Is the issue repeating? [User - Author](20190506) Yes it is a repeating issue, and the oil is leaking under the rotating seal, even RTD is applied at new build
98 | Closed |  | CAT-2 | [5 empty] | RB211 |  |  |  | abradable seal failure | Yes | erosion corrosion oxidisation | none | found with borescope |  | Gasunie |  | 2017.48-60 | S.Broomfield |  |  | [Siemens] (2018) Possibly linked to corrosion. See corrosion presentation from 2017. Please provide further information to allow Siemens to form a comprehensive response. E.g. ESN, when event occurred, engine hours, any RCA information, Siemens RCI or salesforce reference.
80 | Closed |  | CAT-3 |  |  |  |  | 24G62 | RB211 - 24G - DF | Power Gen | Other | Enclosure / Auxiliaries | Main lube oil system pressure drops | No | Failed/failing gearbox-driven oil pump | Low lube oil pressure | Pump replaced during maintenance |  | Shell Global Solutions |  |  | D.Brown |  |  | [Users Steering Committee] User, need more information - after how many hours ? [Siemens] (2018) More information required to form a comprehensive response. Additionally, please provde more information as to the issue, i.e. did the package trip due to low lube oil pressure? Did the auxiliary (if present?) lube oil pump start on annuniation of low lube oil pressure alarm? Did replacement of the gearbox driven pump cure the issue? Has the pump been overhauled / RCA carried out? [User - Author](20190405) Not able to trace back origin of this problem. Propose item to close.
44 | Closed |  | CAT-3 |  |  |  |  | 24G62 | RB211 - 24G - DF | Power Gen | Enclosure / Auxiliaries | Exhaust System | Ripped exhaust bellows | No | Vibration | High temperature in the local area | No work in local area, limited running of unit |  | Shell Global Solutions |  |  | D.Brown |  |  | [Siemens] (2018) From Siemens : Please provide further information to allow Siemens to form a comprehensive response. E.g. ESN, when event occurred, engine hours, any RCA information, Siemens RCI or salesforce reference. [User - Author](20190405) BOV duct failed due to vibration. Duct replaced, item closed.
54 | Closed |  | CAT-3 |  |  |  |  | 24G56, 24G62 | RB211 - 24G - DF | Power Gen | Fuel | Fuel Valve | seized valve | Yes | Fuel quality | Start fail and change to liquid fuel | Valve replaced |  | Shell Global Solutions |  |  | R.Gibbins |  |  | [Siemens] (2018) There are several issues which can lead to failed transfer to liquid fuel or starts on liquid. Liquid Fuel contamination is the most common issue and can lead to sticking of the valve dp regulator. This ultimately requires the replacement of the valve or regulator dp cell to resolve. Other issues encountered include pump ware, fuel leaks, incorrect start settings, ignition systems problems, sticking weight distributors, incorrect valve curve. We have also seen some issues of timing on units which have been retrofitted with the Electric FMV and FT125 control system. These issue need to be investigated on a case by case basis. [User - Author](20190405) Issue resolved. Item closed.
55 | Closed |  | CAT-3 | [5 empty] | RB211 24C | Power Gen | Fuel | Fuel Valve | Trip on fuel transfer | Yes | PCV slow to respond to load changes | trips on fuel transfers | valve replaced and controller tuned |  | Shell Global Solutions |  |  | R.Gibbins |  |  | [Siemens] (2018) Refer to item 54. From Siemens : Please provide further information to allow Siemens to form a comprehensive response. E.g. ESN, when event occurred, engine hours, any RCA information, Siemens RCI or salesforce reference. [User - Author](20190405) PCV replaced, item closed.
42 | Closed |  | CAT-3 |  |  |  |  | 24G56, 24G62 | RB211 - 24G - DF | Power Gen | Enclosure / Auxiliaries | Other | Seal air / cooling air to PT supply failure | No | Failure of flexible hose to engine generated debris that blocked supply | High temperature alarm | Dissassemble and clean debris from system |  | Shell Global Solutions |  |  | D.Brown |  |  | [Users Steering Committee] this is a maintenance issue what is the expected life ? Is there a standard procedure ? Siemens should provide guidance on flexible hose [Siemens] (2018) Flexible Hose inspection schedule should be implemented as for other flexible hoses on the GT package. FHA's (Flexible Hose Assemblies) should be replaced on condition, alternatively PAB 01-0014 provides information on managing FHA's over the lifetime of the plant. Turbo Bulletin 0083 provides the recommended installation procedure for this particular FHA. [User - Author](20190405) System cleaned, item closed.
67 | Closed | [9 empty] | Fuel | Liquid Fuel Valves/Control Cards | Durability, valves & failure of control cards (FT110 control system only) |  |  |  | Fuel quality often cited but not applicable for control cards |  | British Petroleum
13 | Closed | CAT-2 | [5 empty] | 24G62 | RB211-24G-RT62 |  | Compressor | Bearings | lube oil leakage from front bearing O´ring |  |  | leakage outside the engine | Mod 1 removal to change the O´ring (MOD RB211-1623 ) | 02 events : - 35.598 operation hours - 41.597 operation hours | Petrobras | [5 empty] | [Users Steering Committee] can be expected after 40khrs
14 | Closed | CAT-1 | [5 empty] | 24GT62 | RB211-24GT RT62 | Compressor Drive | Compressor | Blades | HPC Blade stg 4 Failure | Yes | Inconclusive, pos DOD | Extended overhaul time | replaced with new parts |  | Equinor |  | 2017.23-27 | S Broomfield | 2017.13-16 |  | [Siemens] (2017) Not aware of any HPC stg 4 failures in last 10+ years on G rated engines. Siemens has been made aware of a recent stg 4 blade failure on a GT engine. However currently we have no information on the cause.
25 | Closed | CAT-2 | [5 empty] | 24G62 | 24G62 | RR | Compressor | Blades | HPC Stage 4 Pitting at Blade Root |  |  | none | none |  | Total |  | 2017.48-60 | S Broomfield | 2017.52 |  | [TCT] (2017) Is this a common issue? Do we see high fallout due to this during inspection?
15 | Closed | CAT-1 | [5 empty] | 24G56, 24G62, 24GT61, 24GT62 | All | All | Compressor | Blades | IPC Stg1 disc, IPC Stg 6-7 disc, HPC stg 3 disc, pitting/erosion/ bolt holes corrosion | No |  |  |  |  | Equinor |  | 2017.48-60 | S Broomfield | 2017.26-28
1 | Closed | CAT-1 | [5 empty] | 24GT61, 24GT62, DLE | RB211-24G-T DLE | RR | Combustion | DLE System | High combustor noise + emissions | Yes | x-gap setting on build of the gas turbine | deterioration in operability | removed engine at last resort. resolved in 2016 via unit removal & rebuild of the ‘x-gap’ | Initialy high noise, then non-compliant emissions, as noise control protected the unit by raising TPZ. In 2014 | E.ON |  | 2017.85-87 | S Broomfield | 2017.37-46 |  | [Siemens] (2017) Majority of DLE's achieve full overhaul lives with aceptable noise and emissions. High numbers of starts and cycles can result in wear to DCN which then opens gaps and changes noise and emissions characteristics. Monitoring of noise levels also recommended with possible remapping required if noise increases. When gas chromatagraphs not used changes in gas composition can also effect combustion temps. Once significant wear has ocurred remapping is unlikely to be able to return to acceptable noise and emissions. In this case discharge nozzles may need to be replaced. [TCT] (2017) DLE slides, testing/optimization, repaired/overhauled hardware not as good as new. Spare hardware necessary for testing and operations. Re-mapping for seasonal changes; field CP103 noise kit???
2 | Closed | CAT-1 | [5 empty] | 24GT61, 24GT62, DLE | RB211-24G-T DLE | RR | Combustion | DLE System | Lack of downturn margin | In process | x-gap setting on build of the gas turbine | unable to part load the unit | resolved in 2016 via unit removal & rebuild of the ‘x-gap’ | in 2014 | E.ON |  | 2017.85-86 | B. Nolan | 2017.48 |  | [TCT] (2017) Inherant on GT DLE's due to short pot design characteristics. Vey little ability to 'tune'/optimize this during build/test.
86 | Closed | CAT-1 | [5 empty] | 24G56, 24G62 | RB211 - 24G - DF | Power Gen | System | Enclosure / Auxiliaries | BOV duct failure | No | vibration induced failure | loss of containment of hot air | replace part |  | Shell Global Solutions |  | 2017.130-132 | R. Gibbins
36 | Closed | CAT-1 | [5 empty] | 24GT61, DLE | RB-21124GT61 | Siemens (Rolls Royce) | Enclosure / Auxiliaries | Fire Fighting System | CO2 shot | No | high temperature in enclousure | CO2 discharge | propose temperature detectors change position | because trip turbine from max load CO2 bottles discharge because high temperature in enclosure | Europac |  | 2017.120-129 | R Gibbins |  |  | [Siemens] (2017) See presentation We are not seeing a fleet issue with the location of the heat detectors triggering false fire suppression release in the reported fleet data. Further information is required to understand the backgrounds to this site issues but we will cover the topic during day 2 of the conference. [TCT] (2017) Establish root cause of the high temperature indication. Ventilation system? package hot spots? Sensor locaiton? Do you have infra-red sensors also?
4 | Closed | CAT-1 | [6 empty] | RB211 | Phase One packages | Combustion | Gas Injectors | Errosion of Phase One package injectors and cracking in liners | Yes | liquids in fuel gas | hot spots and errosion and cracking | supperheat gas as much as possible but at least 20C, however this is not always possible. | From out experience with Phase two combustors in the same service, they are more robust and able to handle the liquids which shows Siemens could modify the design for the Package One combustors to help handle the liquids. | Exxon Mobil |  | 2017.78-80 | S Broomfield |  |  | [Siemens] (2017) PH2 is more tolerant due to swirler burner. Not possible to modify gas only burner to this standard. Either provide correct super heat for gas composition or upgrade to complete Ph2 combustion system. However note that even Ph2 will not completely prevent overheating issues if gas quality is low.
18 | Closed | CAT-1 | [5 empty] | 24G56, 24G62 | RB211-24G | All | Compressor | Inlet Guide Vane (IGV) | Machine trip IGV out of position | In process | feedback, electrical control issues, manufacture | Start failure and or machine trip | Recalibration + component change | Apparent known issue with fleet, still no solution provided by Siemens | Equinor, Centrica |  | 2017.92-107 | R Gibbins | 2017.8 |  | [Siemens] (2017) Fleet data has shown that VIGV issues have been a significant cause of unit disruption over recent years. There have been several improvements to the documentation supporting maintenance and troubleshooting and several software improvements are in development. A presentation will be provided on Day 2 of the conference covering this topic. [TCT] (2017) LVDT or RVDT system? RVDT upgrade Mod is available. VIGV's are known to be a limiting factor on reliability. Carry out good preventative maintenance on the system. See SB0200. Ensure good oil condition. Manually activate and move system. Check trunnion & spigots. Ensure cleanliness around these components and lubrication where required. Carry out annaul function test and times stroke tests. [Users Steering Committee] updates, see item #28
7 | Closed | CAT-1 | [5 empty] | 24G56 | 24G56 | RR | Combustion | Liners | Hot Corrosion on Combustion Chamber Liners | Yes | Hot Corrosion | liner exchange every 6000 to 8000 running hours | Unsatisfactory mitigation measures which consist in liner exchanges every 6000 to 8000 running hours |  | Total |  | 2017.69-73 | S Broomfield |  |  | [Siemens] (2017) This is applicable to one particular operator who have very high sulphur levels in the gas fuel. Revised coating on heatshields has given significant benefit over last ~5 years and customer upgrade to intake has given further improvement. GG lives improved from <4K to over 8K with higher hours likely to be possible. [TCT] (2017) Review Fuel quality. Check burner condition. Review EGT profile, does it indicate high spread or potential hot spots. Is it the same areas on the liners that deteriorate each time? Potentially review effectiveness of the repairs.
99 | Closed | CAT-1 | [5 empty] | 24G56, 24G62, DLE | 1790 - RB 211 24G DLE | Cooper Rolls | Control | Logic | Shutdown due to high pressure difference dP on central bearing due to high viscosity of GG lube oil | In process | low central bearing oil pressure difference dP value and short time to settle down | Shutdown due to high pressure difference dP on central bearing due to high viscosity of GG lube oil | Siemens FSR dP limit raise, or prolonged time to settle down, or both |  | Eustream |  | 2017.108-119 | R Gibbins | 2017.83 |  | [Siemens] (2017) See presentation High Centre bearing dP isn't a common issue on the later PMP LO Systems as far as we know from the Fleet data. High dP on the MkIII LO system during start-up on cold ambient days is more common and several improvements have been developed to address the situation. 1. Trace Heating of the oil line to the engine L1 interface, Reference Service Bulletin 45. 2. Relocation of the oil supply temperature RTD from the LOC to the L1 engine interface. We will be presenting on this topic further during day two of the conference. [TCT] (2017) Critical engine parameter. Understand why your lube oil has high viscosity. When was the last time you changed it? Do you get it analysed on a regular basis? Normally a 10-15% change in viscosity from base value would warrant an oil change. Do you have correct oil heating? Is it working? Is the oil pipework lagged and/or trace heated? H21 filter to Mood LO Scheduling Valve, is it clean?
19.1 | Closed | CAT-1 | [5 empty] | 24G56 | RB211-24G-RT56 | All | Compressor | Rotor | Corrosion/erosion | No | Air intake system/salt | Scrap of parts | new parts |  | Equinor |  | 2017.48-60 | S Broomfield | 2017.31-33 |  | [TCT] (2017) Corrosion issues & High scrap rate. Review TLRF and history with Jeremy
19.2 | Closed | CAT-1 | [5 empty] | 24G56, 24G62 | RB211-24G | All | Compressor | Rotor | IP&HP Stub shaft corrosion | No | Salt carry over | Corrosion/erosion | replaced with new parts |  | Equinor |  | 2017.48-60 | S Broomfield | 2017.31-33 |  | [TCT] (2017) Corrosion issues & High scrap rate. Review TLRF and history with Jeremy
10 | Closed | CAT-1 | [5 empty] | 24G56, 24G62 | RB211 | 24G / compression train | Compressor | Vanes | LP7 exit guide vanes feet breaking off and damaging the HP Compression section. | Yes | Poor LP7 exit guide vane fome injection coverage for dampening of blade vibration. Possible deterioration from high operating temperatures. | Internal object damage to HP section of the compression. Unable to start engine as it would go into surge with damaged compression section. | Evaluate repair procedure and QA for the foam injection. Borescope RB211 fleet HP comp section. Investigate operating temp limitations on foam. | HP comp blades dented, chipped, brocken & failed. Rub between rotating and stationary parts of the ID of the guide vanes and the IP7 blades. Other damage to turbine section and stator/rotor rubs which could have been due to resulting multiple surge events. | Exxon Mobil |  | 2017.62-67 | S Broomfield | 2017.35 |  | [Siemens] (2017) See presentation. Only 7 failures in 20 years / 15m hours but has been subject to recent extensive investigation. Cause primarily ocurrs in high power + high ambient operation. Damping rubber degrades more quickly which results in small increments of wear which are difficult to detect at overhaul. Resolution is to replace shroud rings at overhaul and to fully overhaul the OGV vanes to replace the hard coating. PAB being drafted to advise of issue.
60.1 | Closed | CAT-2 | [5 empty] | 24GT62 | RB211-24GT RT62 | Compressor Drive | Fuel | Fuel Supply | Fuel Gas low temp start up | Yes | Possibly lack of purge. Off engine issue with the fuel gas package arrangement. | Start-up problem |  |  | Equinor |  |  | R Gibbins |  |  | [Siemens] (2017) A minimum fuel gas temperature is required to protect against the formation of liquids within the fuel system. The control system will be set to shutdown if the minimum fuel gas temperature set point is not achieved. Many projects have fuel gas heaters to ensure that the correct temperature is maintained. In some cases is can be difficult to achieve the temperature requirements during start-up especially if the heaters are some distance from the unit. In these cases it may be possible to purge the fuel gas for a short period prior to start up or it may be possible to add a short delay to the low temperature shutdown for unit start up. Siemens would be able to comment further on the specific case if required. [TCT] (2017) Is fuel supply pipework lagged and/or heat traced?
60.2 | Closed | CAT-2 | [5 empty] | 24GT61 |  |  | Fuel | Fuel Supply | Fuel Gas low temp start up |  | Possibly lack of purge. Off engine issue with the fuel gas package arrangement. | Start-up problem |  |  | British Petroleum |  |  | R Gibbins |  |  | [Siemens] (2017) A minimum fuel gas temperature is required to protect against the formation of liquids within the fuel system. The control system will be set to shutdown if the minimum fuel gas temperature set point is not achieved. Many projects have fuel gas heaters to ensure that the correct temperature is maintained. In some cases is can be difficult to achieve the temperature requirements during start-up especially if the heaters are some distance from the unit. In these cases it may be possible to purge the fuel gas for a short period prior to start up or it may be possible to add a short delay to the low temperature shutdown for unit start up. Siemens would be able to comment further on the specific case if required. [TCT] (2017) Is fuel supply pipework lagged and/or heat traced?
47 | Closed | CAT-2 | [5 empty] | 24G56, 24G62 | RB211-24G | All | Enclosure / Auxiliaries | Lube Oil System | LO system 4 way valve failure | No |  | Unplanned stop | replace with new parts |  | Equinor |  |  | R Gibbins | 2017.9 |  | [Siemens] (2017) We have seen some issues of sticktion with the later style LO selector valve. This is currently under investigation but preliminary findings conclude that water contamination of the LO system is a contributing factor leading to corrosion of the valve shuttle. Siemens would need further information of the specifics of the issue encountered to be able to comment further. We will aim to share the findings of the fleet investigation at future Working Together Meetings. [TCT] (2017) Not common to see issues with this part. How long had it been installed for? Root Cause Analysis would need to be carried out to determine the root of the failure. Was it the valve sticking or was it a fault with the actuator? Bench Testing would be required.
46 | Closed | CAT-2 | [5 empty] | 24G56 | RB211-24G-RT56 | All | Enclosure / Auxiliaries | Lube Oil System | Lube oil pump failure | No | Hours of operation vs condition | Start-up problem | replaced pump |  | Equinor |  |  | R Gibbins |  |  | [Siemens] (2017) There have been some failures of the Cascon oil pumps per the PMP LOC design. These failures have tended to occur early in the life of the pump, with a number of the failures occurring during installation and commissioning activities. Some time ago Siemens introduced a pump with increased internal clearances to prevent further failures reference Turbo Bulletin 135. [TCT] (2017) Which type of Lube Oil Pump do you run? Was an RCA done when the pump was sent for repair to determine failure mode? This would be recommended.
49 | Closed | CAT-2 | [5 empty] | 24G56, 24G62, 24GT61, 24GT62 | RB211-24G/GT | All | Enclosure / Auxiliaries | Other | Air intake efficiency | No | Salt carry over | Corrosion/erosion | replaced with new parts |  | Equinor |  | 2017.48-60 | S Broomfield |  |  | [Siemens] (2017) Ref cat 1 item 19 [TCT] (2017) Root Cause of corrosion? (salt,dust, chemical) Review frequency of replacement of pre-filters/secondary filters.
101.1 | Closed | CAT-2 | [5 empty] | 24G56, 24G62, DLE | 1790 - RB 211 24G DLE | Cooper Rolls | Other | Other | Fail to meet new LCP BREF emission limit | No | obsolete combustion system | Unable to run engine | upgrade combustion system | If LCP BREF will be approved as is for older engines this emission limits will be prescribed : daily average - Nox 65 mg/m3, CO not set, Yearly average - Nox 60 mg/m3 CO 60 mg/m3 | Eustream | [5 empty] | [Siemens] (2017) Our latest standard of DLE (dry low emissions) combustion system, the short-can variable split fuelling DLE combustor, is capable of achieving, on gas fuel, 25vppm (51.4 mg/Nm3) NOx at all conditions operating in DLE pre-mix mode on the RB211 G or GT. It can simultaneously achieve <48vppm (<60 mg/Nm3) CO at baseload on the RB211 G or GT . An optional modification can also be fitted to bleed a fraction of High Pressure Compressor air to also achieve <48vppm CO at baseload and at part-load conditions. It is possible to retrofit G and GT RB211 engines to this standard of combustion system if LCP BREF restrictions come into play on installed units in the field. For upgrade of RB211 A, C or G units, an alternative attractive option is to upgrade to the long-can variable split fuelling DLE combustor. This a hybrid DLE solution developed in 2015 of the older long-can combustor but with the variable split fueling of the modern short-can. Although this has a slightly increase NOx signature at higher powers compared to the short-can, it can also achieve <60 mg/Nm3 NOx requirements on the A, C or G RB211 and may limit or eliminate the need for HP compressor bleed for CO control, depending on a given customers turn-down requirements, compared to the short-can. Customers should contact the Siemens Services Mods and Ups team for details. A survey of the package will be required to understand retrofit requirements (e.g. DLE gas fuel skid installation space, needs for part-load HP Compressor bleed valve, best-optimization for long-can or short-can, etc).
38 | Closed | CAT-2 | [6 empty] | RB211 | multiple | Enclosure / Auxiliaries | Other | Fails to start, pressure regulating valves sticking or leaking with o-ring failures | Yes | O-rings and backing rings being cut or extruded, improper materials (to soft) or to loose and being squeezed into side port and sliced off during installation. Also multiple starting issues due to valves sticking caused by varnish or contamination in valves. Complex system with two pressure regulating relief valves in series with the same set point for relief making it difficult to identify where the issue is. | Insufficient pressure or flow of hydraulic fluid to starter. Flow leaking or bypassing the starter. Engine times out or has crash engagement | Replacing valve with engine change out or when leaking. | O-ring and backing ring failures is recent with sticking valves more common in the past | Exxon Mobil |  |  | R Gibbins |  |  | [User] (2017) Just this week did tests with starting block showing as the PRV is screwed into the block the o-rings and back up rings are extruded into the vent port. Depending on how much of the gasket gets extruded it can get damaged or cut. Solution recommended by the customer is to ensure the vent ports in the block are drilled above the chamfer area in place of half way through the chamfer where the o-ring is being squeezed into position. In term solution for existing blocks we are trying hard derometer o-rings and smaller/tighter with more stretch to help prevent the extrusion into the side vent drill port. [Siemens] (2017) Limited information to be able to comment specifically. Siemens would welcome further information and discussion to be able to comment further on a specific issue. [TCT] (2017) Loss of hydraulic supply to Starter Motor causeing starter to dis-engage and crash protection logic to trip unit. Understand more the issue with the pressure regulating valve, maybe discuss with valve OEM. Issues with PCV setup have been experienced in the past. Pressure set too low and bypasses to tank earlier than expected. Possibly review PCV setup. Are the correct replacement parts being installed?
37 | Closed | CAT-2 | [5 empty] | 24GT61, DLE | RB-21124GT61 | Siemens (Rolls Royce) | Enclosure / Auxiliaries | Other | gearbox enclosure | In process | roof is welded | more time needed for open roof in overhaul |  |  | Europac | R Gibbins |  |  |  |  | [Siemens] (2017) From the information provided it sounds like the Gearbox is within an enclosure with a welded roof making it difficult to remove the Gearbox lid for inspection. This isn't a typical configuration for current projects but may have been for older units. Siemens can offer further guidance on the best approach to undertaking gearbox inspecting or the possibility in modifying the package to allow for better or easier access.
48 | Closed | CAT-2 | [5 empty] | 24G56 | RB211-24G-RT56 | All | Enclosure / Auxiliaries | Other | Hydraulic starter failures | Yes | Repair process | Unplanned stop | Starter repair |  | Equinor |  |  | R Gibbins |  |  | [Siemens] (2017) Typically issues effecting the Hydraulic start system include sticking of strocker valves controlling swash plate angle and oil leaks, failures of the Hydraulic starter itself are less common. Siemens would need further information of the specifics of the issues encountered to be able to comment further. [TCT] (2017) What was the nature of the failure? Ensure they are overhauled at a max interval of 500 cycles (50k hours i.e when you send your engine for overhaul). Ensure the starter motor/gearbox gets overhauld too. Use OEM approved overhaul vendor. Maintain good oil quality to protect internal components and seals.
77 | Closed | CAT-2 | [5 empty] | 24GT61, DLE | RB-21124GT61 | Siemens (Rolls Royce) | Other | Other | Island mode | In process | engine is in overspeed | not possible put engine in island mode when main breaker open |  |  | Europac | R Gibbins |  |  |  |  | [Siemens] (2017) This is not an issue which is common across the Industrial RB211 fleet. Siemens would need further information of the specifics of this installation to be able to comment further. [TCT] (2017) High Voltage Specialist required.
100 | Closed | CAT-2 | [5 empty] | 24G56, 24G62, DLE | RB211 24G DLE | Cooper Rolls | Control | Other | MOOG EMV Faulire | No | Fault Resolver, -15V Supply Fault, Fault Card Positioner | Engine ShutDown | Replace | MOOG EMV is installed to the aluminum Ex. Box, which is situated outside of the enclosure in the engine hall. Shut Down engines from the same reason all the time. Overheating of the MOOG controller components. | Eustream |  |  | R Gibbins |  |  | [Siemens] (2017) There have been a number of reported failures across the fleet of Moog motor controllers driving the EMVs. Investigation onto a number of controller failures has concluded a primary root cause of over temperature. This can occur due to several factors such as: inappropriate location of the controller, incorrect mounting, incorrect controller type, metering valve faults etc. This issues is more prevalent on controllers mounted in the hazardous area enclosure where the controller is not fitted with a fan and heat is dissipated through the controller cold plate and through the rear of the enclosure. Mounting of the controller is therefore critical and requires the correct amount of heat transfer past to be applied to the base of the controller. Siemens can provided additional information with reference to STI258. Later controllers are fitted with additional heat sinks on the 15V regulators. Siemens and its vendors are also in the process of developing a replacement controller which is expected to be available later in the year / early 2018. [TCT] (2017) Commom Problem noticed over the fleet. Ensure you have spares. Design Issue. Ensure when controller is installed that heat dissipating compund is applied to the JB backplate. Other options involve moving each controller (DLE) to separate EX. Box to reduce compounded heat. Another option would be to move the controller position to a non-hazardous location, where they can be installed in a normal junction box with ventilation fans to aid cooling. Both of these would be costly and incur large downtime periods.
21 | Closed | CAT-2 | [5 empty] | 24G56, 24G62 | RB211-24G | All | Compressor | Rotor | Gear shaft wear | No | Gear shafts typical wear on the contact surface between the gear shafts. | Scrap of parts | replaced with new parts |  | Equinor |  |  | S Broomfield | 2017.54-55 |  | [Siemens] (2017) Not aware of any specific issues with gear wear, engine rejections or regular rejection of parts at overhaul. Need more info. Wear of gears is always possible on high life engines.
26 | Closed | CAT-2 | [5 empty] | 24G62 | 24G62 | RR | Compressor | Rotor | High Vibration on Front Bearing after Overhaul | No | none | Delay the start of the engine. | none |  | Total |  |  | S Broomfield | 2017.63-65 |  | [Siemens] (2017) Installed vibration is sometimes higher then testbed which can raise concerns but this is a function of the different mounting arrangement in the berth and does not normally indicate a problem with the engine. Siemens is not aware of any problems with engine rejects / trips etc as a result of vibration unless asociated with a specific mechanical failure. [TCT] (2017) We only have experience with one customer Petrobras with this issue. TCT balancing process has been tightened signigivantly in the last frew years with test results showing improvement.
17 | Closed | CAT-3 | [5 empty] | 24G56, 24G62 | RB211 | 24G / compression train | Compressor | Casing | IP BOV fails and ejects through the side of the Y ducting | Yes | ?? Heat from exhaust cyclic fatigue from operating just above idle BOV opening and closing | BOV valve fractures and is ejected up through the side of the Y ducting. | Clamp installed over BOV to stop valve from ejecting if fails. | Changing failure mode, first BOV legs breaking with cyclic fatigue. Then retaining ring poping out allowing valve body to be ejected (evaluated to be a thermal grouth difference between retaining ring and valve body allow the retaining ring to pope out). | Exxon Mobil |  |  | S Broomfield |  |  | [User] Update: Strong back brace has been installed holding BOV from ejecting and no failures since installed. Piping mods also being procured to install back flow check valve as additional protection for the valve. If Siemens believes the cause is back flow from exhaust why don't we see the issue on sister units with the exact same exhaust design? [Siemens] (2017) Complete failures of the IPBOV are vey rare and have only been seen recently at one operator / site. Believe issue is related to backflow of hot exhaust gas down BOV ducting. Fitting of a NRV has been recommended. [TCT] (2017) Advise to operate away from the BOV opening/closing point. If this is not possible operationally. Take engine above BOV closing point and then come back down in load. There is a hysterisis on the re-opening point. If the operaitonal point is subsequently outwith that hysterisis then a possible adjusmtnet to that could be considered (OEM approval/analysis required)
39 | Closed | CAT-3 | [5 empty] | 24GT61, 24GT62, DLE | RB211 24GT/DLE |  | Enclosure / Auxiliaries | Exhaust System | exhaust hood cracks |  |  |  | welding |  | MVM GTER |  |  | D Brown |  |  | [Siemens] (2017) Occasional cracking is experienced in exhaust hoods, especially those that have experienced long service or inclement operating conditions. No specific cause identified. If surrounding material is sound, weld repair is acceptable.
34 | Closed | CAT-3 | [5 empty] | 24GT61, DLE | RB-21124GT61 | Siemens (Rolls Royce) | Enclosure / Auxiliaries | Filtration System | clean filter system | In process | pipe is released in the roof | no clean filters during several hours/day |  | is needed redesign system | Europac |  |  | R Gibbins |  |  | [Siemens] (2017) Limited information to be able to comment. Siemens would be able to comment further on a specific issue if required.
35 | Closed | CAT-3 | [5 empty] | 24GT61, DLE | RB-21124GT61 | Siemens (Rolls Royce) | Enclosure / Auxiliaries | Filtration System | inlet filters clogging because fog and ice | Yes | fog and cold temperatures | trip engine |  | solved by owner/filter provider | Europac |  |  | R Gibbins |  |  | [Siemens] (2017) Siemens can offer anti-icing solutions using HP3 bleeds and can consider heat tracing in some cases. We have also worked with our intake vendors on snow hoods and IR Anti-ice heating elements. Siemens would welcome further discussion of the topic and if necessary conducts a site study to propose a suitable solution. [TCT] (2017) Look at alternate filtration systems.
50 | Closed | CAT-3 | [5 empty] | 24G56, 24G62 | RB211-24G | Cooper Package - Mechanical driver (gas production E&P) | Fuel | Fuel Valve | Drift on fuel valve preventing gas turbine starting reliably | In process | drift of fuel valve rvdt feedback device | Gas turbine start failures | re calibration of fuel valve, adjustment of control stsem fuel flow control parameters. |  | British Petroleum, Centrica |  |  | R Gibbins |  |  | [Users Steering Committee] recommend using latest valve design [Siemens] (2017) This isn't an issue commonly seen with the later electrically actuated fuel valves. If this is an issue with hydraulically actuated valves it may be that the issue is with the LVDT card rather than the valve. These cards as used with the FT100 and FT110 control systems are now obsolete. Siemens would be able to comment further on a specific case if required. [TCT] (2017) Incorrect cabling between the valve and controller causing valve chattering and wear to the valve mechanical internals. (see STI086) Hardened grease on the worm-screw internal to the valve. This can cause over torque (Current pull from the valve) when the valve attempts to operate over this and also cause the valve to fail to close all together (See TB156). Valve seal damage if vent port is plugged. When the port is plugged, it is possible to capture a small volume of gas at system. pressure between the upper and lower seals. This gas may reverse flow across the lower seal when the fuel system is vented, which has the potential to damage the seal. A modification to pipe the vent port to the fuel gas vent line should be carried out (see STI-109). Other Issues could be electrical noise, high controller gains, or incorrect wiring. Ensure you are using the latest valves. See PIB 01-0001
61 | Closed | CAT-3 | [5 empty] | 24GT61, 24GT62 | RB211-24GT RT62 | Compressor Drive | Fuel | Fuel Valve | Fuel Valve failing |  | Demand signal variation | Unplanned stop | replace with new parts |  | Equinor, British Petroleum |  |  | R Gibbins |  |  | [Siemens] (2017) There are several variants of fuel metering valves in service, Siemens would need to know which valve type was fitted to be able to comment in detail. We have seen some issues with position feedback on some earlier hydraulic valves. Typically poor grounding or screening is a contributing factor. There are several improvements to the later Electrically Actuated fuel valves Reference TB147 and PIB 01-0001. Siemens would be able to comment further on a specific case if required. [TCT] (2017) Incorrect cabling between the valve and controller causing valve chattering and wear to the valve mechanical internals. (see STI086) Hardened grease on the worm-screw internal to the valve. This can cause over torque (Current pull from the valve) when the valve attempts to operate over this and also cause the valve to fail to close all together (See TB156). Valve seal damage if vent port is plugged. When the port is plugged, it is possible to capture a small volume of gas at system. pressure between the upper and lower seals. This gas may reverse flow across the lower seal when the fuel system is vented, which has the potential to damage the seal. A modification to pipe the vent port to the fuel gas vent line should be carried out (see STI-109). Other Issues could be electrical noise, high controller gains, or incorrect wiring. Ensure you are using the latest valves. See PIB 01-0001
29 | Closed | CAT-3 | [5 empty] | 24GT61, 24GT62, DLE | RB211 24GT/DLE |  | Control | Human Machine Interface (HMI) | Communication problem btw. ECS and PCS | In process | ECS replacement | seems good |  |  | MVM GTER |  |  | R Gibbins |  |  | [Siemens] (2017) We have seen some issues of communications errors with the HMI on FT125 control systems. This is most notable on DLE machines with the early FT125s due to high processor loading on the ECS. Highly loaded networks, particularly on multi unit sites can also have an impact. Upgrading the ECS processor to the L73 may help and a review of the network topology is recommended. [TCT] (2017) Controls Engineer Required to Investigate root cause.
94 | Closed | CAT-3 | [5 empty] | 24G56, 24G62 | RB211-24G-RT56 & 62 | All | Turbine | Other | Gear pump RT56 failing | No | Open | Unplanned stop | replace with new parts |  | Equinor |  |  | D Brown |  |  | [Siemens] (2017) Assume this refers to PT driven pumps rather than gearbox driven pumps as we are unaware of any issues with latter coupled to RT56. If PT driven, we did have some issues some years ago due to variations in pump interfacing causing loading of casings. Changes made to pumps to ensure consistency and jigs used to ensure manifold alignment is correct. Gearbox driven pump issues or other drivers are not unknown but are generally supplied /addressed by the gear OEM. More info required to comment further. [TCT] (2017) These are older style and have been Mod'd out.
91 | Closed | CAT-3 | [6 empty] | RB211 |  | Power Turbine | Seals | Smoking of PT at hot bearing area. | Yes | Water in instrument air causing damage to hot laby seal on PT. Other cases cause was lack of instrument air during idle allowing oil migration into seal area | smoking at PT during operation, oil mist over bearing and hot exhaust, potential for fire. | Eliminating instrument air purge but this can also cause smoking during startup and idle. Limit operation at idle speed. |  | Exxon Mobil | [5 empty] | [Siemens] (2017) No knowledge of water in inst air causing damage to seal but air should be dry. Inst air provision to seal is intended to ensure adequate sealing at low powers, supply of air is not within Siemens supply but requirements are stated on P&ID's. If these requirements met and issues still apparant check correct setiing / carry out seal air test - if supply inadequate check connecting piping for adequate sizing, PRV malfunction, leakage etc. [TCT] (2017) Ensure correct set-up of disc-end bearing seal instrument air. See TB0173. Consider solution for the moisture in your compressed air lines. Cooling plus seperation method. Check laby seal oil loss tell tale pipe. Inspect bearing covers for oil migration.
75 | Closed | CAT-3 | [5 empty] | 24GT62 | RB211-24GT RT62 | Compressor Drive | Instrumentation | Speed | Speed probe difference N2/ Voting |  | Signal variation | Unplanned stop |  |  | Equinor |  |  | R Gibbins |  |  | [Siemens] (2017) There have been reported issues of N2 Speed signal voting alarms across the GT fleet, specifically with the FT125 control system. In addition to the typical wiring, grounding and screening checks Siemens have identified an improved wiring scheme for the frequency input cards and scan rates which have proved effective at some sites. Siemens would be able to comment further on the specific case if required. [TCT] (2017) This has been experienced in the past. Carry out checks of the full N2 speed signal loop. From sensor all the way back to the control system. Experienced intermittent issues previoulsy where suspected root cause was one of the pins on the sensor, When checks were done no major issue noted other than a wobbly pin. Replacement of sensor rectified issue.
74 | Closed | CAT-3 | [5 empty] | 24G56, 24G62 | RB211-24G | All | Instrumentation | Speed | Speed probe IPC failing | No | hours of operation vs condition | Unplanned stop | replace with new parts |  | Equinor |  |  | R Gibbins | 2017.75-77 |  | [Siemens] (2017) Generally the IPC speed probes on the Industrial RB211 have proven to be reliable. Siemens would need further information of the specifics of this installation to be able to comment further. [TCT] (2017) TCT Developed dynamic bench test capability
30 | Closed | CAT-3 | [5 empty] | 24GT61, 24GT62, DLE | RB211 24GT/DLE |  | Control | Unit Control Panel (UCP) | during crank and roll down the oil heater is OFF | Yes |  |  | manuel switch installed |  | MVM GTER |  |  | R Gibbins |  |  | [Siemens] (2017) Typically the LO Heater will be switched on when the Tank temperature is below 30DegC and switched off when above 35DegC. Typically the heater would be on during crank if the LO temperature is below the min setpoint. Again, typically it will be off during the roll down due to the oil being up to temperature following running of the machine. Siemens can look in more detail at this specific case if required. [TCT] (2017) Review Heater Logic. I&C Engineer would be required to review your logic.
33 | Closed |  | CAT-2 | [7 empty] | Control | Control system | FT-125 card failure during power cycle. Controlnet, Devicenet & Ethernet cards are failing |  |  | TB 0174 issued to identify the risk of failure during a power cycle. Need to have a sufficient spares. Three types of Rockwell cards affected: DeviceNet, ControlNet (those two will prevent operation), EtherNet. Glitch can only occur when PLC is switched off and on. Card glitches during self-test sequence | Complete the replacement of ControlNet, DeviceNet, and EtherNet cards on all units utilizing the FT125 control system as per actions defined in TB 0174 |  | British Petroleum
40 | Closed | [6 empty] | 24G56, 24G62, DLE | RB211 - DLE | Compressor | Enclosure / Auxiliaries | Filtration System | Snow fouling of filters | No | inappropriate filtration system | shut down during snow storms | remove filter |  | Shell Global Solutions
57 | Closed | [6 empty] | 24G62 | RB211 - 24G - DF | Power Gen | Fuel | Fuel Valve | Failed start | No | Closed limit switch on new LFMV's not correctly set. | No permissive to start ignition | Adjusted limit switch in the field |  | Shell Global Solutions
58 | Closed | [6 empty] | 24G62 | RB211 - 24G - DF | Power Gen | Fuel | Fuel Valve | Unit shutdown and blackout | In process | Low voltage supply to FMV | FMV controller shutdown the engine | FMV replaced. FMV power supplies replaced. |  | Shell Global Solutions
31 | Closed | [6 empty] | 24G62 | RB211 - 24G - DF | Power Gen | Control | Inlet Guide Vane (IGV) | VIGV difference alarm | No | Failed Entronics feedback card | "GG Guide Vane RVDT 2 Position Fault" LFF75GGIGVF2 and "RVDT B Full Range Position Alarm" LAA65UC041 | Spares required. Failed part now believed to be obsolete |  | Shell Global Solutions
41 | Closed | [6 empty] | DLE | RB211 - DLE | Compressor | Enclosure / Auxiliaries | Lube Oil System | cooler reliability | No | component failures | unit unavailable | replace components |  | Shell Global Solutions
87 | Closed | [6 empty] | 24G56, 24G62 | RB211 - 24G - DF | Power Gen | System | Other | Fail to start / achieve full purge | Yes | failure of start package PCV / PSV | unable to start machine | replace PCV |  | Shell Global Solutions
140 | [7 empty] | DLE |  | Turbomach | GG | HP-/ IP-NGVs | The inspection in the workshop after 13.300 OH indicated that all IP NGVs exhibited significant hot spots and that several exhibited platform cracking, TBC degradation and material loss. The IP Seal Segments exhibited significant honeycomb degradation and burning. Several HP NGVs exhibited outer platform TBC degradation and cracking and inner platform wear; qty. 1 was sentenced to scrap due to the outer platform being burnt through and for exhibiting associated outer platform cracking and TBC loss. The HP Seal Segments exhibited burning and heavy cutting of the honeycombs | In progess | unknown | All HP/ IP NGVs and IP-/ HP Seal Segments had to be repaired or replaced with new ones. |  | Found during the 8k inspection | Stadtwerke Muenster | Rainer Böschen