## Slide 1: Part-load performance of Natural Gas Combined Cycles integrated with post-combustion CO2 capture
Master thesis – Project main features and design assumptions
Simona Calenda
Prof. Emanuele Martelli
Ing. Lorenzo Pilotti
Ing. Andrea Zelaschi
Dept. Of Energy

## Slide 2: NGCC with Post-combustion CO2 capture
Modelling

## Slide 3: NGCC design
State-of-the-art Natural Gas Combined Cycle (NGCC) with three-pressure level HRSG
H-class Gas Turbine technological level (different sizes may be considered starting from a large-size model)
Two approaches considered for the design of the NGCC:
  Retrofit of H-class NGCC (conventional design)
  Greenfield H-class NGCC with post-combustion CO2 capture and storage
Software: Thermoflex 31
Fig.1 Process layout, natural gas combined cycle (NGCC), without CO2 capture. [1]

## Slide 4: CO2 capture and compression section design
State-of-the-art absorption process using monoethanolamine (MEA) as solvent
Model validated by researchers of GECOS group of Politecnico di Milano
Pressure needed for solvent regeneration: 3 bar (evaporation temperature: 133.5°C)
Software: Aspen Plus 14
Fig.2 NGCC with steam extraction for CO2 capture from the crossover between IP and LP steam turbines. [1]

## Slide 5: Strategies for steam extraction
Retrofit of H-class NGCC:
Following the sliding pressure part-load regulation of the HRSC (design LP pressure level of 6 bar), we identifiy the minimum load of the NGCC with post-combustion CCS (load at which the LP pressure becomes 3 bar)
Greenfield H-class NGCC:
Increased design pressure for LP pressure level (example: 10 bar)
Throttling-valve at crossover section (fixed LP pressure level)
Controlled admission for LP turbine
Steam compressor
Steam ejector

## Slide 6: Natural Gas Combined Cycle
Modelling assumptions
Design point results

## Slide 7: Power plant layout

## Slide 8: Input data Gas Turbine
H-class Gas Turbine model | Ansaldo GT-36-S5
Rotational GT speed [rpm] | 3000
Inlet air temperature [°C] | 15
Inlet air pressure [bar] | 1.013
Inlet air R.H [%] | 60
Fuel composition [mol%] CH4 C2H6 C3H8 C4H10 C5H12 CO2 N2 | 89.0 7.0 1.0 0.1 0.01 2.0 0.89
Fuel LHV [MJ/kg] | 46.506
Fuel inlet temperature [°C] | 15
Fuel inlet pressure [bar] | 45
Fuel temperature [°C] | 200
Nominal Power output: 515 MW
Nominal exhaust gas mass flow rate: 1015 kg/s

## Slide 9: HRSG layout

## Slide 10: HRSG layout
Deaerator
LP level: 1 EVA, 2 SH

## Slide 11: HRSG layout
Deaerator
LP level: 1 EVA, 2 SH
IP level: 1 ECO, 1 EVA, 1 SH, 2 RH sections

## Slide 12: HRSG layout
Deaerator
LP level: 1 EVA, 2 SH
IP level: 1 ECO, 1 EVA, 1 SH, 2 RH sections
HP level: 3 ECO, 1 EVA (Once Through Boiler), 3 SH sections

## Slide 13: HRSG layout
Deaerator
LP level: 1 EVA, 2 SH
IP level: 1 ECO, 1 EVA, 1 SH, 2 RH sections
HP level: 3 ECO, 1 EVA (Once Through Boiler), 3 SH sections
Fuel preheated with IP water from ECO IP 2

## Slide 14: Input data for HRSG
P condensation [bar] | 0.04
HRSG pressure drop [Pa] | 3500
Rotational ST speed [rpm] | 3000
HP pressure [bar] | 185
IP pressure [bar] | 43
LP pressure [bar] | 6
HP SH outlet temperature [°C] | 603.7
RH outlet temperature [°C] | 602
LP SH outlet temperature [°C] | 325
ΔT approach point [°C] | 25
ΔT pinch point [°C] | 8
ΔT sub cooling [°C] | 5
Some steam/water side outlet temperatures of HRSG banks have been assumed (see appendix)
Part-load regulation: sliding pressure
Steam turbines and pumps performance maps from Thermoflex
Water-cooled condenser

## Slide 15: Design Results – Main output data
Parameter | Value
Fuel mass flow rate [kg/s] | 26.43
Exhaust gas mass flow rate [kg/s] | 1014.9
TOT [°C] | 628.7
T stack [°C] | 81.06
Condensate mass flow rate [kg/s] | 177.1
HP steam generated [kg/s] | 120.0
IP steam generated [kg/s] | 21.77
LP steam generated [kg/s] | 23.61
Exhaust gas composition [mol%] O2 CO2 H2O N2 Ar | 11.314 4.474 9.309 74.013 0.891
Parameter | Value
Gas turbine power output [MW] | 515.67
Gas turbine LHV efficiency [%] | 41.95
Steam turbine power output [MW] | 248.08
Steam cycle efficiency [%] | 38.45
Plant gross power [MW] | 763.75
Total auxiliaries and transformer losses [MW] | 18.08
Plant net power [MW] | 745.67
Net electric LHV efficiency [%] | 60.66

## Slide 16: Design Results – Plots
Fig.3 HRSG T-Q diagram
Fig.4 Fuel heater T-Q diagram

## Slide 17: Design Results – Plots
Fig.5 Mollier diagram of steam turbine expansion

## Slide 18: CO2 capture and compression section
Modelling assumptions

## Slide 19: Power plant layout

## Slide 20: Power plant layout
Direct Contact Cooler
Absorption column
Water wash section
Regeneration column
Reboiler
Condenser
CO2 compression section

## Slide 21: Input data CO2 absorption process
Reboiler temperature [°C] | 120
Exhaust gas temperature at absorption column inlet [°C] | 33
Absorption column pressure [bar] | 1.1
Stripping column pressure [bar] | 2
ΔT minimum lean-rich heat exchanger [°C] | 8
Lean solvent composition [mass%] MEA H2O CO2 | 29.1 66.6 4.3
Absorption and regeneration columns type | Packed columns filled with Koch Glitsch Flexipac 2X
Absorption column height [m] | 20
Absorption and regeneration columns diameter | Set to avoid flooding
Carbon capture ratio [%] | 90
Model validated replicating three experimental runs from the Technology Centre Mongstad (TCM) [2], [3], [4].
e-NRTL thermodynamic model used for the electrolyte system
Rate-based approach for the absorption and regeneration column
Equilibrium-based approach for the wash section column and reboiler

## Slide 22: Input data CO2 absorption process
Reboiler temperature [°C] | 120
Exhaust gas temperature at absorption column inlet [°C] | 33
Absorption column pressure [bar] | 1.1
Stripping column pressure [bar] | 2
ΔT minimum lean-rich heat exchanger [°C] | 8
Lean solvent composition [mass%] MEA H2O CO2 | 29.1 66.6 4.3
Absorption and regeneration columns type | Packed columns filled with Koch Glitsch Flexipac 2X
Absorption column height [m] | 20
Absorption and regeneration columns diameter | Set to avoid flooding
Carbon capture ratio [%] | 90
Given the fluid model, the geometric characteristics of the column, pressure drops, temperature specifications of the heat exchangers, thermodynamic conditions of the absorption and regeneration columns, flue gas and lean solvent mass flow rate (or L/G ratio), and reboiler duty, the system returns mass flow rates and composition of the outlet flows (CCR)

## Slide 23: Input data CO2 compression section
Fluid model | Peng-Robinson EOS
Number of intercooled compressors | 4
Compressor isentropic efficiency [%] | 85
Intercooler outlet temperature [°C] | 40
CO2 delivery pressure [bar] | 110

## Slide 24: Next steps
Full-load simulation of the NGCC with post-combustion CO2 capture (retrofit case)
Part-load analysis of the NGCC with post-combustion CO2 capture (retrofit case) with identification of minimum load
Full-load and part-load analysis of the greenfield NGCC with post-combustion CO2 capture (steam compressor)
Full-load and part-load analysis of the greenfield NGCC with post-combustion CO2 capture (throttling valve at crossover section)

## Slide 25: Thank you for your attention

## Slide 26: Appendix
Tout steam SH_HP3 [°C] | 603.7
Tout steam RH2 [°C] | 602
Tout steam SH_HP2 [°C] | 550
Tout steam RH1 [°C] | 510
Tout steam SH_HP1 [°C] | 480
Tout steam SH_LP2 [°C] | 325
Tout water ECO_HP2 [°C] | 320
Tout steam SH_LP1 [°C] | 220
Tout water ECO_HP1 [°C] | 240
Steam/Water outlet temperatures assumed for the design of the HRSG banks

## Slide 27: Reference list
[1] K.Jordal, PA. Marchioro Ystad, R. Anantharaman, A. Chikukwa, and O. Bolland. “Design-point and part-load considerations for natural gas combined cycle plants with post combustion capture”. In: Elsevier (2012), pp. 271–282.
[2] E. S. Hamborg et al., “Results from MEA testing at the CO2 Technology Centre Mongstad. Part II: Verification of baseline results,” Energy Procedia, vol. 63, pp. 5994–6011, Jan. 2014, doi: 10.1016/J.EGYPRO.2014.11.634.
[3] P. Loldrup Fosbøl et al., “Results of the fourth Technology Centre Mongstad campaign: LVC testing,” International Journal of Greenhouse Gas Control, vol. 89, pp. 52–64, Oct. 2019, doi: 10.1016/J.IJGGC.2019.06.025.
[4] E. Gjernes et al., “Documenting Modes of Operation with Cost Saving Potential at the Technology Centre Mongstad,” SSRN Electronic Journal, Oct. 2020, doi: 10.2139/SSRN.3366235.